## Sheet 1-Project Information
1.Component | Military Construction Program Electronic Security Systems (ESS) Budget Estimator Ver 1.0 |  | 2. Date
Navy |  |  | 2007-11-21
3. Installation and Location/UIC |  | 4. Project Title
ESS Project
5. Category Code | 6. Project Number | 7. User Defined | 8.User Defined
9. User Input
Facility
A. Enter the size of the facility in square feet. |  |  | 10000
|  |  |  | 1 | 100000000
B. Enter the number of floors. |  |  | 1
|  |  |  | 1 | 125
C. Does this project include exterior (building façade) access control (i.e. card readers at exterior doors into the facility)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
D. Does this project include interior volumetric sensors (i.e. interior mounted motion detectors) in areas other than the interior CAA's or SCIF's? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
E. Does this project include interior closed circuit TV in areas other than the interior CAA's or SCIF's? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
Building Perimeter
F. Does this project include exterior (building façade) volumetric sensors (i.e. exterior mounted motion detectors protecting critical exterior assets)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
G. Does this project include exterior (building façade) closed circuit TV (i.e. building mounted cameras viewing exterior doors and around the building)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
Site Perimeter
H. Does this project include exterior (site perimeter) access control (i.e. card readers at perimeter vehicle or pedestrian gates)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
I. Does this project include exterior (site perimeter) intrusion detection (i.e. buried or fence mounted intrusion sensors)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
J. Does this project include exterior (site perimeter) closed circuit TV (i.e. cameras viewing perimeter boundary of site)? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
K. Enter length of perimeter fence to be protected in linear feet. |  |  | 0
|  |  |  | 0 | 100000000
Interior Enclaves
L. Does this project include interior Sensitive Compartmented Information Facility's (SCIF's)? How many? |  |  | 0
|  |  |  | 0 | 100
M. Enter the average size of the interior SCIF's in square feet. |  |  | 0
|  |  |  | 0 | 0
N. Does this project include interior Controlled Access Areas (CAA's) in addition to SCIF's? How many? |  |  | 0
|  |  |  | 0 | 100
O. Enter the average size of the interior CAA's in square feet. |  |  | 0
|  |  |  | 0 | 0
Site Specifics
P. Does this project include local monitoring (at the facility) or remote monitoring (at a central monitoring station) of the electronic security system? Enter Locally, Remotely, or Both. |  |  | Locally
|  |  |  | Please Select | Locally | Remotely | Both
Q. Does this project warrant biometric devices for access control? Enter Yes or No. |  |  | No | Please Select | Yes | No
R. Does this project warrant thermal imaging for the closed circuit television cameras? Enter Yes or No. |  |  | No
|  |  |  | Please Select | Yes | No
S. Does this project warrant video analytics/video content analysis for perimeter intrusion detection? Enter Yes or No" |  |  | No
|  |  |  | Please Select | Yes | No
T. What is the overall Level of Protection requirement of the facility? Enter Low, Medium, or High. |  |  | Low
|  |  |  | Please Select | Low | Medium | High

## Sheet 2-Project Budget Summary
1.Component | Military Construction Program Physical Security Equipment Budget Estimator Tool |  |  | 2. Date
Navy |  |  |  | 2007-11-21
3. Installation and Location/UIC |  |  | 4. Project Title
0 |  |  | ESS Project
5. Category Code | 6. Project Number | 7. User Defined | 8. User Defined | 9. Project Cost
0 | 0 | 0 | 0 | 0
COST ESTIMATE
System |  | Supporting Infrastructure | PSE Equipment | Total
Controlled Access Areas |  | 0 | 0 | 0
Sensitive Compartmented Information Facilities |  | 0 | 0 | 0
Interior Intrusion Detection Zones |  | 0 | 0 | 0
Interior Closed Circuit Television Zones |  | 0 | 0 | 0
Exterior (Bldg Façade) Access Control Zones |  | 0 | 0 | 0
Exterior (Bldg Façade) Intrusion Detection Zones |  | 0 | 0 | 0
Exterior (Bldg Façade) CCTV Zones |  | 0 | 0 | 0
Perimeter Access Control Zones |  | 0 | 0 | 0
Perimeter Intrustion Detection Zones |  | 0 | 0 | 0
Perimeter Closed Circuit Television Zones |  | 0 | 0 | 0
Biometric Access Control Zones |  | 0 | 0 | 0
Thermal Imaging Zones |  | 0 | 0 | 0
Video Analytic Zones |  | 0 | 0 | 0
Exterior (Bldg Façade) Monitored Door Zones |  | 0 | 0 | 0
ACS Local Monitoring Zones |  | 0 | 0 | 0
CCTV Local Monitoring Zones |  | 0 | 0 | 0
ACS Remote Monitoring Zones |  | 0 | 0 | 0
CCTV Remote Monitoring Zones |  | 0 | 0 | 0
SUBTOTAL |  | 0 | 0 | 0
User Input (only applied to PSE Equipment)
1. ACF | 1 |  | 0 |  | 0.01 | 5
2. Contingency | 5 | % | 0 |  | 0.01 | 100
3. SIOH | 8 | % | 0 |  | 0.01 | 20
4. Escalation | 1 |  | 0 |  | 1 | 1.5
User Input (for OCONUS Mobilization/Per Diem)
5. OCONUS | 0 |  | 0
TOTAL |  | 0 | 0 | 0
Total OP Request | 0
Total MILCON Request | 0

## Sheet 3-Zone Count
Note
Interior square footage less SCIF's and CAA's | 10000
Estimated length (ft) of building perimeter | 560 | [6 empty] | 19
Estimated number of exterior pedestrian doors | 12 | [6 empty] | 20
Zone Size/Count Factors
System | Total Zones | Base Zones | Incr. Zones | Unit | Low Risk | Medium Risk | High Risk | Note
Controlled Access Area (CAA) | 0 | 0 | 0 | Ea | 1 | 1 | 1 | 1
Sensitive Compartmented Information Facility (SCIF) | 0 | 0 | 0 | Ea | 1 | 1 | 1 | 2
Interior Intrusion Detection Zone | 0 | 0 | 0 | Sf | 15400 | 7700 | 3850 | 3
Interior Closed Circuit Television Zone | 0 | 0 | 0 | Sf | 15400 | 7700 | 3850 | 4
Exterior (Bldg Façade) Access Control Zone | 0 | 0 | 0 | Ea | 0.25 | 0.25 | 0.1 | 5
Exterior (Bldg Façade) Intrusion Detection Zone | 0 | 0 | 0 | Lf | 400 | 200 | 100 | 6
Exterior (Bldg Façade) Closed Circuit Television Zone | 0 | 0 | 0 | Lf | 600 | 300 | 300 | 7
Perimeter Access Control Zone | 0 | 0 | 0 | Lf | 1 | 1 | 1 | 8
Perimeter Intrusion Detection Zone | 0 | 0 | 0 | Ea | 300 | 300 | 300 | 9
Perimeter Closed Circuit Television Zone | 0 | 0 | 0 | Lf | 600 | 600 | 300 | 10
Biometric Access Control Zone | 0 | 0 | 0 | Ea | 1 | 1 | 1 | 11
Thermal Imaging Zone | 0 | 0 | 0 | Lf | 3280 | 3280 | 1640 | 12
Video Analytic Zone | 0 | 0 | 0 | Ea | 1 | 1 | 1 | 13
Exterior (Bldg Façade) Monitored Door Zone | 0 | 0 | 0 | Ea | 1 | 1 | 1 | 14
ACS Local Monitoring Zone | 0 | 0 | 0 | Ea | 32 | 32 | 32 | 15
CCTV Local Monitoring Zone | 0 | 0 | 0 | Ea | 16 | 16 | 16 | 16
ACS Remote Monitoring Zone | 0 | 0 | 0 | Ea | 32 | 32 | 32 | 17
CCTV Remote Monitoring Zone | 0 | 0 | 0 | Ea | 16 | 16 | 16 | 18
Notes
1. Number of zones provided by User on Project Information sheet. No size adjustment; implies cost of ESS for 1,000 SF CAA is the same as a 10,000 SF CAA.
2. Number of zones provided by User on Project Information sheet. No size adjustment; implies cost of ESS for 1,000 SF SCIF is the same as a 10,000 SF SCIF.
3. Number of zones determined by dividing the building square footage net of SCIF's and CAA's by the appropriate factor based on risk level. Risk level and building square footage provided by User on Project Information sheet. Number of zones rounded up the next whole number. Detection zone size for Bosch DS939 is 70' x 360-degrees (3,848 SF). Low risk detection provides 1 SF of detection per 4 SF of interior space (I.e. 1 detector per 15,400 SF). Medium risk provides 1 SF of detection per 2 SF of interior space (1 detector per 7,700 SF). High risk provides 1 SF of detection per 1 SF of interior space (1 detector per 3,850 SF). Otherwise stated: Low risk provides 25% interior coverage, medium risk 50%, and high risk 100%.
4. Number of zones determined as in number 3 above. Associate interior CCTV zones with interior IDS zones. Provides 1 camera per interior IDS zone.
5. Number of zones determined by multiplying estimated number of exterior pedestrian doors by appropriate factor based on risk level. Risk level provided by User. Number of zones rounded up to the next whole number. High risk facility provided with fewer entry points than Low and Medium risk facilities. High risk provides 1 entry point for every 10 exterior pedestrian doors. Low and Medium risk provides one entry point per 4 exterior pedestrian doors.
6. Number of zones determined by dividing the estimated building perimeter length by the appropriate factor based on risk level. Risk level provided by User on Project Information sheet. Number of zones rounded up the next whole number. Detection zone size for ProTech SDI-77XL-MIL is 100' x 10'. Low risk detection provides 1 LF of detection per 4 LF of building perimeter (I.e. 1 detector per 400 LF of building perimeter). Medium risk provides 1 LF of detection per 2 LF of building perimeter (1 detector per 200 LF of building perimeter). High risk provides 1 LF of detection per 1 LF of building perimeter (1 detector per 100 LF of building perimeter). Otherwise stated: Low risk provides 25% building perimeter coverage, medium risk 50%, and high risk 100%.
7. Number of zones determined by dividing the estimated building perimeter length by the appropriate factor based on risk level. Risk level and building square footage provided by User on Project Information sheet. Number of zones rounded up the next whole number. Detection zone size based on military standard CCTV zone size of 300' and 600'. Low risk provides 1 camera per 600 LF of building perimeter. Medium and High risk provides 1 camera per 300 LF of building perimeter. For High Risk facilities, a CCTV zone is also provided for each exterior (building facade) ACS Zone.
8. Number of zones set at 4 for all projects requiring perimeter ACS zones (I.e. card readers at perimeter vehicle gates).
9. Number of zones determined by dividing the site perimeter length by the appropriate factor based on risk level. Site perimeter length and risk level provided by User on Project Information sheet. Number of zones rounded up the next whole number. Detection zone size based on military standard IDS zone size of 300'. All risk categories provide detection around the entire perimeter. Low and Medium risk provide 1 layer of protection. High risk provides 2 levels of protection.
10. Number of zones determined by dividing the site perimeter length by the appropriate factor based on risk level. Site perimeter length and risk level provided by User on Project Information sheet. Number of zones rounded up the next whole number. Detection zone based on military standard CCTV zone size of 300' and 600'. Low and Medium risk provides 1 camera per 600 LF of site perimeter. High risk provides 1 camera per 300 LF of site perimeter
11. Number of zones is the total number of access control zones in project. Includes SCIF's, CAA's, exterior (building façade) ACS, and exterior (site perimeter) ACS zones.
12. Number of zones determined by dividing the site perimeter length by the appropriate factor based on risk level. Site perimeter length and risk level provided by User on Project Information sheet. Number of zones rounded up to the next whole number. Viewing range of EMX-8000 is 1 km (3280') for human sized object. Assume thermal cameras will only be utilized along the site perimeter and complete perimeter coverage is required. Low and Medium risk provide 1 camera per 3280 LF (1 km) of site perimeter. High risk provides 1 camera per 1640 LF (.5 km) of site perimeter.
13. Number of zones is the total number of exterior closed circuit television zones in project less thermal imaging zones. Includes exterior (building façade and site perimeter) CCTV zones.
14. Number of zones determined by subtracting number of Exterior (Building Façade) ACS zones from estimated number of exterior pedestrian doors.
15. Number of zones determined by dividing the number of ACS zones (less CAA and SCIF ACS zones because they have their own workstation) by appropriate factor based on risk level. Factor is constant because each workstation can only support 32 card reader controlled doors (zones). Workstation can support unlimited IDS zones
16. Number of zones determined by dividing the number of CCTV zones (less CAA and SCIF ACS zones because they have their own workstation) by appropriate factor based on risk level. Factor is constant because each workstation can only support 16 CCTV cameras (zones).
17. Same as #15 above
18. Same as #16 above
19. Estimated length of building perimeter based on square footage of building and number of floors. Calculation assumes building is square or rectangular in shape. Correction factor of 40% added to estimated length based on in-house data compiled for this project.
20. Estimated number of exterior pedestrian doors based on estimated length of building perimeter (see note 19). Assumes one door per 50 linear feet of building perimeter based on in-house data compiled for this project.

## Sheet 4-Zone Budget Summary
| Low Risk |  | Medium Risk |  | High Risk
System | Supporting Infrastructure | ESS Equipment | Supporting Infrastructure | ESS Equipment | Supporting Infrastructure | ESS Equipment
Controlled Access Area | 4344.692 | 14842.1552 | 8424.3335 | 16598.3189 | 16981.1923 | 38856.7415
SCIF | 25140.4753 | 40000.4602 | 25140.4753 | 40000.4602 | 25140.4753 | 40000.4602
Interior Intrustion Detection Zone
Base (minimum) Cost | 2852.2863 | 3929.7319 | 2852.2863 | 3929.7319 | 2852.2863 | 3929.7319
Incremental Cost per Zone | 1359.8805 | 517.6463 | 1359.8805 | 517.6463 | 1359.8805 | 517.6463
Interior Closed Circuit Television Zone
Base (minimum) Cost | 4344.692 | 16120.8416 | 4344.692 | 16120.8416 | 4344.692 | 16120.8416
Incremental Cost per Zone | 1359.8805 | 1001.3745 | 1359.8805 | 1001.3745 | 1359.8805 | 1001.3745
Exterior (Building Façade) Access Control Zone
Base (minimum) Cost | 2852.2863 | 6133.425 | 2852.2863 | 6133.425 | 2852.2863 | 6133.425
Incremental Cost per Zone | 1359.8805 | 3494.041 | 1359.8805 | 3494.041 | 1359.8805 | 3494.041
Exterior (Building Façade) Intrustion Detection Zone
Base (minimum) Cost | 2852.2863 | 4477.6804 | 2852.2863 | 4477.6804 | 2852.2863 | 4477.6804
Incremental Cost per Zone | 1359.8805 | 1029.2343 | 1359.8805 | 1029.2343 | 1359.8805 | 1029.2343
Exterior (Building Façade) CCTV Zone
Base (minimum) Cost | 2852.2863 | 3841.541 | 2852.2863 | 3841.541 | 2852.2863 | 3841.541
Incremental Cost per Zone | 1359.8805 | 3518.735 | 1359.8805 | 3518.735 | 1359.8805 | 3518.735
Perimeter Access Control Zone
Base (minimum) Cost | 6115.9995 | 5502.6778 | 6115.9995 | 5502.6778 | 6115.9995 | 5502.6778
Incremental Cost per Zone | 4623.5937 | 2527.1778 | 4623.5937 | 2527.1778 | 4623.5937 | 2527.1778
Perimeter Intrustion Detection Zone
Base (minimum) Cost | 7608.59 | 21056.0312 | 7608.59 | 21056.0312 | 14136.386 | 25319.2544
Incremental Cost per Zone | 6116.1843 | 11497.8287 | 6116.1843 | 11497.8287 | 12643.9803 | 21151.7559
Perimeter CCTV Zone
Base (minimum) Cost | 7187.1228 | 13347.0108 | 7187.1228 | 13347.0108 | 7187.1228 | 13347.0108
Incremental Cost per Zone | 7187.1228 | 7493.4268 | 7187.1228 | 7493.4268 | 7187.1228 | 7493.4268
Biometric Adder | 0 | 1588.466 | 0 | 1588.466 | 0 | 1588.466
Thermal Imaging Adder | 0 | 45437.8414 | 0 | 45437.8414 | 0 | 45437.8414
Video Analytics Adder | 0 | 5382.168 | 0 | 5382.168 | 0 | 5382.168
Exterior (Building Façade) Montiored Door
Base (minimum) Cost | 2852.2863 | 3640.7687 | 2852.2863 | 3640.7687 | 2852.2863 | 3640.7687
Incremental Cost per Zone | 1359.8805 | 228.6831 | 1359.8805 | 228.6831 | 1359.8805 | 228.6831
ACS Local Monitoring Zone
Base (minimum) Cost | 1492.4058 | 7963.923 | 1492.4058 | 7963.923 | 1492.4058 | 7963.923
Incremental Cost per Zone | 0 | 4110.0345 | 0 | 4110.0345 | 0 | 4110.0345
CCTV Local Monitoring Zone
Base (minimum) Cost | 2984.8115 | 19617.0876 | 2984.8115 | 19617.0876 | 2984.8115 | 19617.0876
Incremental Cost per Zone | 0 | 13678.3471 | 0 | 13678.3471 | 0 | 13678.3471
ACS Remote Monitoring Zone
Base (minimum) Cost | 2984.8115 | 14843.3835 | 2984.8115 | 14843.3835 | 2984.8115 | 14843.3835
Incremental Cost per Zone | 0 | 10989.495 | 0 | 10989.495 | 0 | 10989.495
CCTV Remote Monitoring Zone
Base (minimum) Cost | 5969.623 | 48123.7691 | 5969.623 | 48123.7691 | 5969.623 | 48123.7691
Incremental Cost per Zone | 0 | 36246.2881 | 0 | 36246.2881 | 0 | 36246.2881

## Sheet 5-Zone Budget Detail
USER INPUT
1. Enter Subcontractor's Material Markup1 |  |  | 10 | 1 | 50
2. Enter Subcontractor's Equipment Markup2 |  |  | 10 | 1 | 50
3. Enter Electrical Subcontractor's O&P3 |  |  | 49 | 1 | 100
4. Enter General Contractor's Markup4 |  |  | 10 | 1 | 50
CONTROLLED ACCESS AREA (CAA)
A segregated, interior area within a facility where access is controlled via electronic card readers.
LOW RISK
Low risk CAA includes a total of three (3) entry points. One (1) of the entry points is equipped with a card reader and associated access control hardware (balanced magnetic switch, request to exit motion sensor and button, magnetic lock), while the other two (2) points are for emergency exit only. Cost includes standalone workstation for administration of access control system and all necessary access control system controllers, modules, enclosures, etc. for a fully operational system. Cost includes all wiring, conduit, and 120 VAC drops required to support equipment. Assumes existing LAN.
|  |  | Supporting Infrastructure |  |  |  | PSE Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Contactless Card Reader with Keypad | Ea | 1 | 0 | 0 | 0 | 0 | 480 | 124.45 | 0 | 784.7736
(HID Prox Pro - 5355)
Contactless Cards | Ea | 150 | 0 | 0 | 0 | 0 | 5.35 | 0 | 0 | 971.025
(HID ISOProx II-1386LGGSN or HID iClass 2002PGGMN)
Balanced Magnetic Switch | Ea | 1 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 121.9693
(GE 1076D)
Request-to-Exit Motion Detector | Ea | 1 | 0 | 0 | 0 | 0 | 64.95 | 146.08 | 0 | 318.0146
(Detection Systems 150i)
Magnetic Lock | Ea | 1 | 0 | 0 | 0 | 0 | 262.95 | 168 | 0 | 593.5215
(Locknetics 390 Plus)
Request-to-Exit Button | Ea | 1 | 0 | 0 | 0 | 0 | 67.95 | 42 | 0 | 151.0575
(Securitron SN-PB5)
Panel and Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 251.25 | 84 | 0 | 441.6885
(Lenel LNL-OLS75CTX)
Battery Back-Up for ACS Panel | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.5 | 0 | 79.827
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Single Card Reader Module | Ea | 1 | 0 | 0 | 0 | 0 | 243.75 | 84 | 0 | 432.6135
(Lenel LNL-1300)
Power Supply for Door Hardware | Ea | 1 | 0 | 0 | 0 | 0 | 114.95 | 84 | 0 | 276.7655
(SDC SZ-602RF)
ACS Workstation with Enrollment | Ea | 1 | 0 | 0 | 0 | 0 | 5671.5 | 672 | 0 | 7963.923
(Lenel PCC-32ESI, CAM500-KUSB, P210, SWC-32ESI)
Wiring 18-2c (door contact, electric lock) | Lf | 300 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 213.4275
(CSC 151000)
Wiring 18-4c (request-to-exits) | Lf | 300 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 242.1045
(CSC 151200)
Wiring 18-6c (card reader) | Lf | 150 | 0 | 0 | 0 | 0 | 0.228 | 0.375 | 0 | 133.5758
(CSC 151230)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(from door to panel, misc @ panel)
120 Volt Drop | Ls | 2 | 382.4 | 628.25 | 0 | 2984.8115 | 0 | 0 | 0 | 0
(1for panel, 1 for workstation)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 4344.692 |  |  |  | 14842.1552
MEDIUM RISK |  |  | Medium Risk
Medium risk CAA includes all equipment included in Low risk CAA with the addition of one (1) interior motion detector and one (1) balanced magnetic switch for each of the emergency exit only doors. Medium risk CAA also provides a card reader with keypad instead of just a standard card reader. Cost includes input module required for motion detector as well as all additional wiring and conduit.
|  |  | Supporting Infrastructure |  |  |  | PSE Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Low Risk Carryover6 | Ls | 1 | 0 | 0 | 0 | 4344.692 | 0 | 0 | 0 | 14842.1552
Contactless Card Reader with Keypad | Ea | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3.63
(HID Prox Pro - 5355)
Interior 360-Degree Motion Detector - Dual Technology | Ea | 1 | 0 | 0 | 0 | 0 | 130 | 146 | 0 | 396.594
(Detection Systems DS-9370)
Balanced Magnetic Switch | Ea | 2 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 243.9386
(GE 1076D)
Input Module for Panel | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL-1100)
Wiring 18-2c (balanced magnetic switches) | Lf | 300 | 0 | 0 | 0 | 0 | 0.082 | 0.38 | 0 | 216.612
(CSC 151000)
Wiring 18-4c (motion detector) | Lf | 150 | 0 | 0 | 0 | 0 | 0.16 | 0.38 | 0 | 122.463
(CSC 151200)
1/2" Rigid Galvanized Conduit | Lf | 450 | 2.44 | 3.73 | 0 | 4079.6415 | 0 | 0 | 0 | 0
(to motion and BMS's)
| Ea | 0 | 0 | 0 | 0 | 0 | 5 | 2.5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 8424.3335 |  |  |  | 16598.3189
HIGH RISK |  |  | High Risk
High risk CAA includes all equipment included in Low and Medium risk CAA with the addition of one (1) interior motion detector, one (1) balanced magnetic switch on the door into the telco closet, and two (2) interior fixed cameras. In addition, cost includes standalone workstation for administration of CCTV system and the necessary CCTV recorder, power supply, and equipment rack. Cost includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Medium Risk Carryover7 | Ea | 1 | 0 | 0 | 0 | 8424.3335 | 0 | 0 | 0 | 16598.3189
Balanced Magnetic Switch | Ea | 1 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 121.9693
(GE 1076D)
Interior 360-Degree Motion Detector - Dual Technology | Ea | 1 | 0 | 0 | 0 | 0 | 130 | 146 | 0 | 396.594
(Detection Systems DS-9370)
Interior Fixed Camera | Ea | 2 | 0 | 0 | 0 | 0 | 490 | 124.45 | 0 | 1593.7471
(Pelco ICS150-CDV4A-incl lens, mount, encl.)
Digital Video Recorder (600GbHD) | Ea | 1 | 0 | 0 | 0 | 0 | 7562.25 | 336 | 0 | 9701.0265
(Lenel DVS-16-S)
Matrix Switcher | Ea | 1 | 0 | 0 | 0 | 0 | 1428 | 336 | 0 | 2278.584
(Pelco CM6700-MXB4, CM9760-CDU-T, PV130)
Keyboard Controller | Ea | 1 | 0 | 0 | 0 | 0 | 583 | 84 | 0 | 843.106
(Pelco KBD300A)
Camera Power Supply and Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 63 | 42 | 0 | 145.068
(Pelco MCS4-2)
17" Flat Screen LCD Monitor | Ea | 1 | 0 | 0 | 0 | 0 | 1268.95 | 10.5 | 0 | 1552.639
(Bosch MON171CL)
Uninterruptible Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 1199.25 | 42 | 0 | 1519.9305
(Powerware 9125 2000)
Equipment Rack | Ea | 1 | 0 | 0 | 0 | 0 | 2500 | 336 | 0 | 3575.704
(Middle Atlantic VRK-44-31H, MW-LVT, PVFD-44, etc)
Wiring 18-4c (motion detector) | Lf | 150 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 121.0523
(CSC 151200)
Coaxial/Power Cable RG-59U with 18/2c (cameras) | Lf | 300 | 0 | 0 | 0 | 0 | 0.612 | 0.38 | 0 | 409.002
(CSC 516681)
1/2" Rigid Galvanized Conduit | Lf | 450 | 2.44 | 3.73 | 0 | 4079.6415 | 0 | 0 | 0 | 0
(to motion, cameras to DVR)
120 Volt Drop | Ls | 3 | 382.4 | 628.25 | 0 | 4477.2173 | 0 | 0 | 0 | 0
(CCTV panel, workstation, DVR/UPS)
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 |  |  |  | 0
TOTALS | [5 empty] | 16981.1923 |  |  |  | 38856.7415
SENSITIVE COMPARTMENTED INFORMATION FACILITY
An accredited area, room, group of rooms, or building where sensitive compartmented information may be stored, used, discussed, or electronically processed. Entry into a SCIF is limited to one (1) entrance which, like a CAA, is controlled via an electronic card reader.
No Risk Category - All SCIF's Considered the Same Risk
SCIF includes one (1) entry point that is protected by a card reader with keypad and associated access control hardware (balanced magnetic switch, request to exit motion sensor and button, magnetic lock). Cost assumes one (1) exterior emergency exit door and two interior doors segregating SCI areas all protected by balanced magnetic switches. Cost includes four (4) interior motion detectors, two (3) fixed interior cameras, a standalone workstation for administration of access control system, and all necessary access control system controllers, modules, and enclosures. Cost includes standalone workstation for administration of CCTV system and the necessary CCTV recorder, power supply, and equipment rack. Cost includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Contactless Card Reader with Keypad | Ea | 1 | 0 | 0 | 0 | 0 | 480 | 124.45 | 0 | 784.7736
(HID Prox Pro - 5355)
.
Proximity Cards | Ea | 25 | 0 | 0 | 0 | 0 | 5.35 | 0 | 0 | 161.8375
(HID ISOProx II-1386LGGSN or HID iClass 2002PGGMN)
Balanced Magnetic Switch | Ea | 5 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 609.8466
(GE 1076D)
Request-to-Exit | Ea | 1 | 0 | 0 | 0 | 0 | 64.95 | 146.08 | 0 | 318.0146
(Detection Systems 150i)
Request-to-Exit Button | Ea | 1 | 0 | 0 | 0 | 0 | 67.95 | 42 | 0 | 151.0575
(Securitron SN-PB5)
Magnetic Lock | Ea | 1 | 0 | 0 | 0 | 0 | 262.95 | 168 | 0 | 593.5215
(Locknetics 390 Plus)
Panel and Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 251.25 | 84 | 0 | 441.6885
(Lenel LNL-OLS75CTX)
Battery Back-Up for ACS Panel | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.5 | 0 | 79.827
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Single Card Reader Module | Ea | 1 | 0 | 0 | 0 | 0 | 243.75 | 84 | 0 | 432.6135
(Lenel LNL-1300)
Power Supply for Door Hardware | Ea | 1 | 0 | 0 | 0 | 0 | 114.95 | 84 | 0 | 276.7655
(SDC SZ-602RF)
ACS Workstation with Enrollment | Ea | 1 | 0 | 0 | 0 | 0 | 5671.5 | 672 | 0 | 7963.923
(Lenel PCC-32ESI, CAM500-KUSB, P210, SWC-32ESI)
Interior 360-Degree Motion Detector - Dual Technology | Ea | 3 | 0 | 0 | 0 | 0 | 130 | 146 | 0 | 1189.782
(Detection Systems DS-9370)
Input Module for Panel | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL-1100)
Interior Fixed Camera | Ea | 3 | 0 | 0 | 0 | 0 | 490 | 124.45 | 0 | 2390.6206
(Pelco ICS150-CDV4A-incl lens, mount, encl.)
Digital Video Recorder (600GbHD) | Ea | 1 | 0 | 0 | 0 | 0 | 7562.25 | 336 | 0 | 9701.0265
(Lenel DVS-16-S)
Matrix Switcher | Ea | 1 | 0 | 0 | 0 | 0 | 1428 | 336 | 0 | 2278.584
(Pelco CM6700-MXB4, CM9760-CDU-T, PV130)
Keyboard Controller | Ea | 1 | 0 | 0 | 0 | 0 | 583 | 84 | 0 | 843.106
(Pelco KBD300A)
Camera Power Supply and Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 63 | 42 | 0 | 145.068
(Pelco MCS4-2)
17" Flat Screen LCD Monitor | Ea | 1 | 0 | 0 | 0 | 0 | 1268.95 | 10.5 | 0 | 1552.639
(Bosch MON171CL)
Uninterruptible Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 1199.25 | 42 | 0 | 1519.9305
(Powerware 9125 2000)
Equipment Rack | Ea | 1 | 0 | 0 | 0 | 0 | 2500 | 336 | 0 | 3575.704
(Middle Atlantic VRK-44-31H, MW-LVT, PVFD-44, etc)
Wiring 18-2c | Lf | 1050 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 746.9962
(CSC 151000)
Wiring 18-4c | Lf | 750 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 605.2613
(CSC 151200)
Wiring 18-6c | Lf | 150 | 0 | 0 | 0 | 0 | 0.228 | 0.375 | 0 | 133.5758
(CSC 151230)
Coaxial/Power Cable RG-59U with 18/2c | Lf | 450 | 0 | 0 | 0 | 0 | 0.612 | 0.38 | 0 | 613.503
(CSC 516681)
1/2" Rigid Galvanized Conduit | Lf | 1950 | 2.44 | 3.73 | 0 | 17678.4465 | 0 | 0 | 0 | 0
(to motion and BMS's, door to panel)
120 Volt Drop | Ls | 5 | 382.4 | 628.25 | 0 | 7462.0288 | 0 | 0 | 0 | 0
(ACS panel & workstation, CCTV panel & workstation, DVR)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 25140.4753 |  |  |  | 40000.4602
TYPICAL INTERIOR INTRUSION DETECTION ZONE
Typical interior intrusion detection zone provides protection of interior space with a dual technology, panoramic motion detector.
LOW, MEDIUM, AND HIGH RISK
Typical interior intrusion detection zone includes a dual technology, panoramic motion detector designed for interior use. Cost includes panel, power supply, and all modules required. Cost also includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Panel and Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 251.2 | 84 | 0 | 441.628
(Lenel LNL-OLS75CTX)
Battery Back-Up Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.4 | 0 | 79.6631
(Lenel ABT-12)
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Input Module | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL - 1100)
Interior 360-Degree Motion Detector - Dual Technology | Ea | 1 | 0 | 0 | 0 | 0 | 130 | 146 | 0 | 396.594
(Detection Systems DS-9370)
Wiring 18-4c | Lf | 150 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 121.0523
(CSC 151200)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(to motion)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for enclosure)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2852.2863 |  |  |  | 3929.7319
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 517.6463
TYPICAL INTERIOR CLOSED CIRCUIT TELEVISION ZONE
Typical interior closed circuit television zone provides viewing capabilities of interior space via a fixed, interior color camera.
LOW, MEDIUM, AND HIGH RISK
Typical interior closed circuit television zone includes an interior fixed camera for viewing and a digital video recorder for storage and playback. Cost includes panel, power supply, and equipment rack. Cost also includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Interior Fixed Camera | Ea | 1 | 0 | 0 | 0 | 0 | 490 | 124.45 | 0 | 796.8736
(Pelco ICS150-CDV4A-incl lens, mount, encl.)
Digital Video Recorder (600GbHD,supports 16 cameras) | Ea | 1 | 0 | 0 | 0 | 0 | 7562.25 | 336 | 0 | 9701.0265
(Lenel DVS-16-S)
Camera Power Supply and Enclosure (supports 16 cameras) | Ea | 1 | 0 | 0 | 0 | 0 | 153 | 84 | 0 | 322.806
(Pelco MCS16-20)
Uninterruptible Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 1199.25 | 42 | 0 | 1519.9305
(Powerware 9125 2000)
Equipment Rack | Ea | 1 | 0 | 0 | 0 | 0 | 2500 | 336 | 0 | 3575.704
(Middle Atlantic VRK-44-31H, MW-LVT, PVFD-44, etc)
Coaxial/Power Cable RG-59U with 18/2c | Lf | 150 | 0 | 0 | 0 | 0 | 0.612 | 0.38 | 0 | 204.501
(CSC 516681)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(from cameras to DVRl)
120 Volt Drop | Ls | 2 | 382.4 | 628.25 | 0 | 2984.8115 | 0 | 0 | 0 | 0
(CCTV power supply, DVR/UPS)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 4344.692 |  |  |  | 16120.8416
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 1001.3745
TYPICAL EXTERIOR (BUILDING FAÇADE) ACCESS CONTROL ZONE
Typical exterior (building façade) access control zone provides electronic access control at an exterior door into a facility.
LOW, MEDIUM, AND HIGH RISK
Typical exterior (building façade) access control zone provides electronic access control at an exterior door into a facility. Cost includes card reader and all associated access control hardware (balanced magnetic switch, request to exit motion sensor and button, magnetic lock). Cost includes all necessary access control system controllers, modules, enclosures, etc. for a fully operational system. Cost includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Contactless Card Reader with Keypad | Ea | 1 | 0 | 0 | 0 | 0 | 480 | 124.45 | 0 | 784.7736
(HID Prox Pro - 5355)
Balanced Magnetic Switch | Ea | 1 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 121.9693
(GE 1076D)
Request-to-Exit Motion Sensor | Ea | 1 | 0 | 0 | 0 | 0 | 64.95 | 146.08 | 0 | 318.0146
(Detection Systems 150i)
Magnetic Lock | Ea | 1 | 0 | 0 | 0 | 0 | 262.95 | 168 | 0 | 593.5215
(Locknetics 390 Plus)
Request-to-Exit Button | Ea | 1 | 0 | 0 | 0 | 0 | 67.95 | 42 | 0 | 151.0575
(Securitron SN-PB5)
Panel and Power Supply (supports 16 readers) | Ea | 1 | 0 | 0 | 0 | 0 | 251.25 | 84 | 0 | 441.6885
(Lenel LNL-OLS75CTX)
Battery Back-Up for ACS Panel | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.5 | 0 | 79.827
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 readers) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Single Card Reader Module | Ea | 1 | 0 | 0 | 0 | 0 | 243.75 | 84 | 0 | 432.6135
(Lenel LNL-1300)
Power Supply for Door Hardware (supports 16 doors) | Ea | 1 | 0 | 0 | 0 | 0 | 401.95 | 84 | 0 | 624.0355
(SDC SZ-636RF)
Wiring 18-2c | Lf | 300 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 213.4275
(CSC 151000)
Wiring 18-4c | Lf | 150 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 121.0523
(CSC 151200)
Wiring 18-6c | Lf | 150 | 0 | 0 | 0 | 0 | 0.228 | 0.375 | 0 | 133.5758
(CSC 151230)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(from door to panel, misc @ panel)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(from door to panel)
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2852.2863 |  |  |  | 6133.425
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 3494.041
TYPICAL EXTERIOR (BUILDING FAÇADE) INTRUSION DETECTION ZONE
Typical exterior (building façade) intrusion detection zone provides motion detection coverage of critical assets located around the exterior of the building (generators, electrical panels and transformers, HVAC intakes, etc).
LOW, MEDIUM, AND HIGH RISK
Typical exterior (building façade) intrustion detection zone provides protection of critical exterior assets through the use of an exterior, dual technology motion detector. Cost includes necessary panel, power supply, and modules as well as all required wiring, conduit, and 120 VAC drops to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Panel and Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 281.25 | 84 | 0 | 477.9885
(Lenel LNL-OLS120CTX)
Battery Back-Up Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.4 | 0 | 79.6631
(Lenel ABT-12)
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Input Module | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL - 1100)
Exterior Dual Technology Motion Detector - 100 Lf Zone | Ea | 1 | 0 | 0 | 0 | 0 | 523 | 168 | 0 | 908.182
(Protech USA SDI-77XL-MIL)
Wiring 18-4c | Lf | 150 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 121.0523
(CSC 151200)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(to motion)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for enclosure)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2852.2863 |  |  |  | 4477.6804
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 1029.2343
TYPICAL EXTERIOR (BUILDING FAÇADE) CLOSED CIRCUIT TELEVISION ZONE
Typical exterior (building façade) closed circuit television zone provides viewing capabilities of critical assets located around the exterior of the building (exterior ACS doors, generators, electrical panels and transformers, HVAC intakes, etc).
LOW, MEDIUM, AND HIGH RISK
Typical exterior (building façade) closed circuit television zone provides viewing capabilities of critical exterior assets through the use of an exterior, pan/tilt/zone color camera. Cost includes necessary panel, power supply, and wall mount as well as all required wiring, conduit, and 120 VAC drops to support system equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Exterior Pan/Tilt/Zoom Camera - 300 Lf Zone | Ea | 1 | 0 | 0 | 0 | 0 | 2421 | 164 | 0 | 3198.206
(Pelco Spectra III SE-SD53CBW-PG-E1 incl, lens, mount, encl.)
Exterior Camera Wall Mount | Ea | 1 | 0 | 0 | 0 | 0 | 39 | 42 | 0 | 116.028
(Pelco MRWA)
Camera Power Supply and Enclosure (supports 16 cameras) | Ea | 1 | 0 | 0 | 0 | 0 | 153 | 84 | 0 | 322.806
(Pelco MCS16-20)
Coaxial/Power/Comm Cable RG-59U with 18/4c | Lf | 150 | 0 | 0 | 0 | 0 | 0.612 | 0.38 | 0 | 204.501
(CSC 516681)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(from cameras to DVRl)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(CCTV power supply)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2852.2863 |  |  |  | 3841.541
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 3518.735
TYPICAL PERIMETER ACCESS CONTROL ZONE
Typical perimeter access control zone provides electronic access control at a site perimeter entrance point (I.e. vehicle gate). This system would typically be integrated with an automatic gate and gate operator.
LOW, MEDIUM, AND HIGH RISK
Typical perimeter access control zone provides electronic access control at a site perimeter entrance point (I.e. vehicle gate). Cost doesn't include automatic gate or gate operator, but rather, only the hardware required to equip an automatic gate with electronic access control. Cost includes necessary panels, power supply, controllers, and modules as well as card reader stanchion and stanchion pad. Cost also includes all required wiring, conduit, and 120 VAC drops to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Contactless Card Reader with Keypad | Ea | 1 | 0 | 0 | 0 | 0 | 480 | 124.45 | 0 | 784.7736
(HID Prox Pro - 5355)
High Security Balanced Magnetic Switch | Ea | 1 | 0 | 0 | 0 | 0 | 84.95 | 63.38 | 0 | 206.6693
(GE SR2707A)
Card Reader Stanchion | Ea | 1 | 0 | 0 | 0 | 0 | 105 | 84 | 0 | 264.726
(Engineered Parking Systems 306-4)
Concrete Pad for Stanchion | CY | 0.185 | 0 | 0 | 0 | 0 | 175 | 99.5 | 0.56 | 69.469
(2'x2'x1')
Panel and Power Supply (supports 16 readers) | Ea | 1 | 0 | 0 | 0 | 0 | 251.25 | 84 | 0 | 441.6885
(Lenel LNL-OLS75CTX)
Battery Back-Up for ACS Panel | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.5 | 0 | 79.827
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 readers) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Single Card Reader Module | Ea | 1 | 0 | 0 | 0 | 0 | 243.75 | 84 | 0 | 432.6135
(Lenel LNL-1300)
6" x 6" x 6" NEMA 4 Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 164 | 84 | 0 | 336.116
(Generic)
Wiring 18-2c | Lf | 480 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 341.484
(CSC 151000)
Wiring 18-6c | Lf | 480 | 0 | 0 | 0 | 0 | 0.228 | 0.375 | 0 | 427.4424
(CSC 151230)
1/2" Rigid Galvanized Conduit | Lf | 510 | 2.44 | 3.73 | 0 | 4623.5937 | 0 | 0 | 0 | 0
(reader and mag to operator, op to encl. and panel)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(to panel)
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 6115.9995 |  |  |  | 5502.6778
INCREMENTAL COST PER ZONE | [5 empty] | 4623.5937 |  |  |  | 2527.1778
TYPICAL PERIMETER INTRUSION DETECTION ZONE
Typical perimeter intrusion detection zone provides protection around the site perimeter to unauthorized personnel.
LOW AND MEDIUM RISK
Low and medium risk perimeter intrusion detection zone provides protection around the site perimeter to unauthorized personnel through the use of a buried fiber optic sensor system. Cost includes necessary outdoor enclosures, panels, modules, cable, processor, and dirt work. Cost includes required wiring, conduit, 120 VAC drops to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Panel and Power Supply (supports 1 zone) | Ea | 1 | 0 | 0 | 0 | 0 | 114.95 | 84 | 0 | 276.7655
(SDC 602RF)
24" x 24" x 10" NEMA 4 Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 2875 | 670 | 0 | 4576.88
(for processor and power supply)
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Input Module (supports 16 zones) | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL - 1100)
Buried Fiber-Optic Sensor Cable -5' x 300' Zone | Lf | 3000 | 0 | 0 | 0 | 0 | 0.85 | 0.5 | 0 | 5544
(Fiber SenSys IC-4)
Buried Sensor Processor (supports 1-300 Lf zone) | Ea | 1 | 0 | 0 | 0 | 0 | 4000 | 336 | 0 | 5390.704
(Fiber SenSys FD-208)
Wiring 18-2c | Lf | 150 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 106.7137
(CSC 151000-from enclosure to panel)
Splice Box at Building | Ea | 1 | 0 | 0 | 0 | 0 | 600 | 336 | 0 | 1276.704
(Generic)
1/2" Rigid Galvanized Conduit | Lf | 300 | 2.44 | 3.73 | 0 | 2719.761 | 0 | 0 | 0 | 0
(from enclosure to zone of detection)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(from enclosure to panel)
Sod Removal and Install | Ls | 1 | 0 | 0 | 0 | 0 | 487.5 | 186.8 | 80.52 | 993.4694
(Generic)
Trenching and Backfill for 1/2" conduit | Lf | 300 | 0.62 | 0.11 | 0.73 | 544.137 | 0 | 0 | 0 | 0
(Generic)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for buried sensor processor)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for panel)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 7608.59 |  |  |  | 21056.0312
INCREMENTAL COST PER ZONE | [5 empty] | 6116.1843 |  |  |  | 11497.8287
HIGH RISK
High risk provides site perimeter protection through the use of both a buried fiber optic sensor system and pairs of exterior, dual technology motion detectors. Cost includes necessary outdoor enclosures, panels, modules, cable, processor, and dirt work. Cost includes required wiring, conduit, 120 VAC drops to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Panel and Power Supply (supports 1zone) | Ea | 2 | 0 | 0 | 0 | 0 | 114.95 | 84 | 0 | 553.531
(SDC 602RF)
24" x 24" x 10" NEMA 4 Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 2875 | 670 | 0 | 4576.88
(for processor and power supply)
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Input Module (supports 16 zones) | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL - 1100)
Buried Fiber-Optic Sensor Cable -5' x 300' Zone | Lf | 3000 | 0 | 0 | 0 | 0 | 0.85 | 0.5 | 0 | 5544
(Fiber SenSys IC-4)
Buried Sensor Processor (supports 1-300' zone) | Ea | 1 | 0 | 0 | 0 | 0 | 4000 | 336 | 0 | 5390.704
(Fiber SenSys FD-208)
Exterior Dual Technology Motion Detector - 300 Lf Zone | Ea | 3 | 0 | 0 | 0 | 0 | 523 | 168 | 0 | 2724.546
(Protech USA SDI-77XL-MIL)
3" Galvanized Pole for Motion Detector | Ea | 3 | 0 | 0 | 0 | 0 | 88.5 | 16.5 | 3.35 | 414.546
(Generic)
Splice Box at Building | Ea | 1 | 0 | 0 | 0 | 0 | 600 | 336 | 0 | 1276.704
(Generic)
Wiring 18-2c | Lf | 150 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 106.7137
(CSC 151000-from buried sensor enclosure to panel)
Wiring 18-4c | Lf | 1050 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 847.3658
(CSC 151200-from motions to panel)
1/2" Rigid Galvanized Conduit | Lf | 1050 | 2.44 | 3.73 | 0 | 9519.1635 | 0 | 0 | 0 | 0
(from zones to enclosure, enc to panel)
Trenching and Backfill for 1/2" conduit | Lf | 900 | 0.62 | 0.11 | 0.73 | 1632.411 | 0 | 0 | 0 | 0
(Generic)
Sod Removal and Install | Ls | 1 | 0 | 0 | 0 | 0 | 487.5 | 186.8 | 80.52 | 993.4694
(Generic)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for panel)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for buried sensor processor)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 14136.386 |  |  |  | 25319.2544
INCREMENTAL COST PER ZONE | [5 empty] | 12643.9803 |  |  |  | 21151.7559
TYPICAL PERIMETER CLOSED CIRCUIT TELEVISION ZONE
Typical perimeter closed circuit television zone provides viewing capabilities of the site perimeter.
LOW, MEDIUM, AND HIGH RISK
Typical perimeter closed circuit television zone provides viewing capabilities of the site perimeter through the use of an exterior, pan/tilt/zoom color camera. Cost includes all necessary exterior enclosures, panels, power supply, camera pole, and dirt work. Cost also includes all required wiring, conduit, and 120 VAC drops to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Exterior Pan/Tilt/Zoom Camera - 300 Lf Zone | Ea | 1 | 0 | 0 | 0 | 0 | 2421 | 164 | 0 | 3198.206
(Pelco Spectra III SE-SD53CBW-PG-E1 incl, lens, mount, encl.)
Exterior Camera Pole Mount | Ea | 1 | 0 | 0 | 0 | 0 | 266 | 42 | 0 | 390.698
(Pelco PP350)
6" x 6" NEMA 4 Enclosure | Ea | 2 | 0 | 0 | 0 | 0 | 164 | 84 | 0 | 672.232
(Generic)
24" x 24" NEMA 4 Enclosure | Ea | 1 | 0 | 0 | 0 | 0 | 2875 | 670 | 0 | 4576.88
(Pelco MCS16-20)
Camera Power Supply and Enclosure (supports 1 camera) | Ea | 1 | 0 | 0 | 0 | 0 | 116 | 84 | 0 | 278.036
(Pelco WCS1-4)
Splice Box at Building | Ea | 1 | 0 | 0 | 0 | 0 | 600 | 336 | 0 | 1276.704
(Generic)
20' Wood Pole | Ls | 1 | 0 | 0 | 0 | 0 | 607.75 | 935.36 | 0 | 2268.4325
(incl. base, excavation, fill, etc.)
Wiring 18-2c | Lf | 25 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 17.7856
(CSC 151000)
Coaxial/Power/Comm Cable RG-59U with 18/2c | Lf | 490 | 0 | 0 | 0 | 0 | 0.612 | 0.38 | 0 | 668.0366
(CSC 516681)
1/2" Rigid Galvanized Conduit | Lf | 490 | 2.44 | 3.73 | 0 | 4442.2763 | 0 | 0 | 0 | 0
(from pole to building, inside building to DVR)
Trenching and Backfill for 3/4" conduit | Lf | 300 | 0.62 | 0.11 | 0.73 | 544.137 | 0 | 0 | 0 | 0
(Generic)
120 Volt Drop | Ls | 1 | 593.8 | 823.5 | 109.5 | 2200.7095 | 0 | 0 | 0 | 0
(at pole, pulled from field)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 7187.1228 |  |  |  | 13347.0108
INCREMENTAL COST PER ZONE | [5 empty] | 7187.1228 |  |  |  | 7493.4268
BIOMETRIC ADDER
Provides additional identification verification at access controlled doors throught the use of a fingerprint reader. Added to base ACS zone cost. Cost is per ACS zone.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Fingerprint Reader | Ea | 1 | 0 | 0 | 0 | 0 | 1199 | 84 | 0 | 1588.466
(Bioscrypt V-Smart-A-H)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 0 |  |  |  | 1588.466
THERMAL IMAGING ADDER
Provides thermal imaging capabilites at site perimeter through the use of thermal imaging camera. Added to base cost of site perimeter CCTV zone. Cost is per CCTV zone.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Thermal Imaging PTZ Camera | Ea | 1 | 0 | 0 | 0 | 0 | 36770 | 168 | 0 | 44767.052
(EMX 8000/2X 100mm-incl mount, control box, etc)
Wiring 18-4c | Lf | 490 | 0 | 0 | 0 | 0 | 0.159 | 0.375 | 0 | 395.4374
(CSC 151200-from camera to panel)
Specialized Training | Ea | 1 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 275.352
(Generic)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 0 |  |  |  | 45437.8414
VIDEO ANALYTICS ADDER
Provides advanced video analytic capabilities to exterior cameras to provide for exterior (building façade and site perimeter) video motion detection. Uses existing cameras with the addition of advanced software, processors, and servers. Added to base cost of exterior (building facade and site perimeter) CCTV zone. Cost is per CCTV zone.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Video Analytics Processor | Ea | 1 | 0 | 0 | 0 | 0 | 900 | 504 | 0 | 1915.056
(Guardian Solutions)
Video Analytics Software | Ea | 1 | 0 | 0 | 0 | 0 | 1500 | 0 | 0 | 1815
(Guardian Solutions)
Camera Calibration | Ea | 1 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 826.056
(Guardian Solutions)
Best Practices/Procedures Training | Ea | 1 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 826.056
(Guardian Solutions)
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | [5 empty] | 0 |  |  |  | 5382.168
TYPICAL EXTERIOR (BLDG FAÇADE) MONITORED DOOR ZONE
Typical exterior (building façade) monitored door provides protection of an exterior door through the use of a balanced magnetic switch.
LOW, MEDIUM, AND HIGH RISK
Typical exterior (building facade) monitored door includes one (1) balanced magnetic switch, panel, power supply, and all modules required. Cost also includes all wiring, conduit, and 120 VAC drops required to support equipment.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Panel and Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 251.2 | 84 | 0 | 441.628
(Lenel LNL-OLS75CTX)
Battery Back-Up Power Supply (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 51.75 | 10.4 | 0 | 79.6631
(Lenel ABT-12)
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 1 | 0 | 0 | 0 | 0 | 405 | 21 | 0 | 524.469
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | 1 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 59.873
(Generic)
System Controller (supports 16 devices) | Ea | 1 | 0 | 0 | 0 | 0 | 812.25 | 336 | 0 | 1533.5265
(Lenel LNL-1000)
Input Module (supports 16 switches) | Ea | 1 | 0 | 0 | 0 | 0 | 525 | 84 | 0 | 772.926
(Lenel LNL - 1100)
Balanced Magnetic Switch | Ea | 1 | 0 | 0 | 0 | 0 | 14.95 | 63.38 | 0 | 121.9693
(GE 1076D)
Wiring 18-2c | Lf | 150 | 0 | 0 | 0 | 0 | 0.08 | 0.375 | 0 | 106.7137
(CSC 151000)
1/2" Rigid Galvanized Conduit | Lf | 150 | 2.44 | 3.73 | 0 | 1359.8805 | 0 | 0 | 0 | 0
(to motion)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(for enclosure)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2852.2863 |  |  |  | 3640.7687
INCREMENTAL COST PER ZONE | [5 empty] | 1359.8805 |  |  |  | 228.6831
ACS LOCAL MONITORING ZONE
ACS Local monitoring zone provides monitoring capabilities of all facility ACS systems locally (I.e. in the facility). Provides monitoring of interior, exterior, and perimeter systems. ACS local monitoring zone is in addition to monitoring workstations provided for CAA's and SCIF's.
Low, Medium, and High Risk
ACS local monitoring station includes PC, software, all licenses, monitor, etc to support 32 card reader controlled doors and unlimited IDS zones. Also includes badging workstation with camera, tripod, badge printer, etc.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
ACS Workstation | Ea | 1 | 0 | 0 | 0 | 0 | 2600.25 | 588 | 0 | 4110.0345
(Lenel PCC-32ESI, SWC-32ESI)
Enrollment Workstation | Ea | 1 | 0 | 0 | 0 | 0 | 3071.25 | 84 | 0 | 3853.8885
(Lenel CAM-500KUSB, P210i-0000U-IDO)
120 Volt Drop | Ls | 1 | 382.4 | 628.25 | 0 | 1492.4058 | 0 | 0 | 0 | 0
(ACS workstation)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 1492.4058 |  |  |  | 7963.923
INCREMENTAL COST PER ZONE | [5 empty] | 0 |  |  |  | 4110.0345
CCTV LOCAL MONITORING ZONE
CCTV local monitoring zone provides monitoring capabilities of all facility CCTV systems locally (I.e. in the facility). Provides monitoring of interior, exterior, and perimeter systems. CCTV local monitoring zone is in addition to monitoring workstations provided for CAA's and SCIF's.
Low, Medium, and High Risk
CCTV local monitoring station includes DVR, matrix switcher, keyboard controller, monitor, etc to support 16 cameras
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Digital Video Recorder (600GbHD) | Ea | 1 | 0 | 0 | 0 | 0 | 7562.25 | 336 | 0 | 9701.0265
(Lenel DVS-16-S)
Matrix Switcher | Ea | 1 | 0 | 0 | 0 | 0 | 1428 | 336 | 0 | 2278.584
(Pelco CM6700-MXB4, CM9760-CDU-T, PV130)
Keyboard Controller | Ea | 1 | 0 | 0 | 0 | 0 | 583 | 84 | 0 | 843.106
(Pelco KBD300A)
17" Flat Screen LCD Monitor | Ea | 1 | 0 | 0 | 0 | 0 | 1268.95 | 10.5 | 0 | 1552.639
(Bosch MON171CL)
Uninterruptible Power Supply | Ea | 1 | 0 | 0 | 0 | 0 | 1199.25 | 42 | 0 | 1519.9305
(Powerware 9125 2000)
CCTV Jumpers | Ea | 16 | 0 | 0 | 0 | 0 | 5.65 | 1.4 | 0 | 146.0976
(Generic)
Equipment Rack | Ea | 1 | 0 | 0 | 0 | 0 | 2500 | 336 | 0 | 3575.704
(Middle Atlantic VRK-44-31H, MW-LVT, PVFD-44, etc)
120 Volt Drop | Ls | 2 | 382.4 | 628.25 | 0 | 2984.8115 | 0 | 0 | 0 | 0
(CCTV workstation and DVR)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2984.8115 |  |  |  | 19617.0876
INCREMENTAL COST PER ZONE | [5 empty] | 0 |  |  |  | 13678.3471
ACS REMOTE MONITORING ZONE
ACS Remote monitoring zone provides monitoring capabilities of all facility ACS systems remotely (I.e. outside the facility). Provides monitoring of interior, exterior, and perimeter systems. ACS remote monitoring zone is in addition to monitoring workstations provided for CAA's and SCIF's.
Low, Medium, and High Risk
ACS remote monitoring station includes PC, software, all licenses, monitor, etc to support 32 card reader controlled doors and unlimited IDS zones. Also includes badging workstation with camera, tripod, badge printer, etc.
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
ACS Workstation | Ea | 1 | 0 | 0 | 0 | 0 | 2100 | 588 | 0 | 3504.732
(Lenel PCC-32ESI - at building)
ACS Server | Ea | 1 | 0 | 0 | 0 | 0 | 4275 | 588 | 0 | 6136.482
(Lenel PCS-32ESI - at CMS)
Software License (32 card readers) | Ea | 2 | 0 | 0 | 0 | 0 | 500.25 | 42 | 0 | 1348.281
(SWC-32ESI)
Enrollment Workstation | Ea | 1 | 0 | 0 | 0 | 0 | 3071.25 | 84 | 0 | 3853.8885
(Lenel CAM-500KUSB, P210i-0000U-IDO)
120 Volt Drop | Ls | 2 | 382.4 | 628.25 | 0 | 2984.8115 | 0 | 0 | 0 | 0
(ACS workstation at building and CMS)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 2984.8115 |  |  |  | 14843.3835
INCREMENTAL COST PER ZONE | [5 empty] | 0 |  |  |  | 10989.495
CCTV REMOTE MONITORING ZONE
CCTV remote monitoring zone provides monitoring capabilities of all facility CCTV systems remotely (I.e. outside the facility). Provides monitoring of interior, exterior, and perimeter systems. CCTV remote monitoring zone is in addition to monitoring workstations provided for CAA's and SCIF's.
Low, Medium, and High Risk
CCTV remote monitoring station includes DVR, matrix switcher, keyboard controller, monitor, etc to support 16 cameras
|  |  | Supporting Infrastructure |  |  |  | ESS Equipment
Description | Unit | Qty | Materials | Labor | Equipment | Total5 | Materials | Labor | Equipment | Total5
Digital Video Recorder (600GbHD) | Ea | 1 | 0 | 0 | 0 | 0 | 7562.25 | 336 | 0 | 9701.0265
(Lenel DVS-16-S)
Matrix Switcher | Ea | 1 | 0 | 0 | 0 | 0 | 1428 | 336 | 0 | 2278.584
(Pelco CM6700-MXB4, CM9760-CDU-T, PV130)
Fiber Transmitter/Multiplexer (4 Ch Video, 1 Ch Data) | Ea | 4 | 0 | 0 | 0 | 0 | 1981.71 | 84 | 0 | 10142.1804
(IFS VT6010DRDT)
Fiber Receiver/Multiplexer (4 Ch Video, 1 Ch Data) | Ea | 4 | 0 | 0 | 0 | 0 | 1981.71 | 84 | 0 | 10142.1804
(IFS VR6010DRDT)
Fiber Transciever (1 Ch Data) | Ea | 2 | 0 | 0 | 0 | 0 | 184.78 | 42 | 0 | 584.8436
(IFS D1010)
Keyboard Controller | Ea | 2 | 0 | 0 | 0 | 0 | 583 | 84 | 0 | 1686.212
(Pelco KBD300A)
17" Flat Screen LCD Monitor | Ea | 2 | 0 | 0 | 0 | 0 | 1268.95 | 10.5 | 0 | 3105.278
(Bosch MON171CL)
Uninterruptible Power Supply | Ea | 2 | 0 | 0 | 0 | 0 | 1199.25 | 42 | 0 | 3039.861
(Powerware 9125 2000)
CCTV Jumpers | Ea | 32 | 0 | 0 | 0 | 0 | 5.65 | 1.4 | 0 | 292.1952
(Generic)
Equipment Rack | Ea | 2 | 0 | 0 | 0 | 0 | 2500 | 336 | 0 | 7151.408
(Middle Atlantic VRK-44-31H, MW-LVT, PVFD-44, etc)
120 Volt Drop | Ls | 4 | 382.4 | 628.25 | 0 | 5969.623 | 0 | 0 | 0 | 0
(CCTV workstation and equipment rack)
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BASE (MINIMUM) COST | [5 empty] | 5969.623 |  |  |  | 48123.7691
INCREMENTAL COST PER ZONE | [5 empty] | 0 |  |  |  | 36246.2881
Notes
1. Material markup as recommended in 2006 RS Means Building Construction Cost Data, Pg 3. Password authorization required for changes.
2. Equipment profit as recommended in 2006 RS Means Building Construction Cost Data, Pg 3. Password authorization required for changes.
3. Electrician loaded rate with O&P of $62.60 per hour/$42.00 per hour bare labor = 49% burden. 2006 RS Means Building Construction Cost Data, inside back cover. Password authorization required for changes.
4. General contractor markup as recommended in 2006 RS Means Building Construction Cost Data, pg 2. Password authorization required for changes.
5. Total cost is calculated as the sum of the bare material cost plus Material Markup (default 10%) for subcontractor profit; the bare labor cost plus subcontractor Labor Overhead and Profit; and the bare equipment cost plus Equipment Markup (default 10%) for subcontractor profit. An additional 10% is then added to this sum to account for general contractor markup.
6. Medium risk CAA includes all items in Low risk CAA plus additional measures outlined.
7. High risk CAA includes all items in Low and Medium risk CAA plus additional measures outlined

## Sheet 6-Pricing References
Description | Unit | Materials | Labor | Equipment
Contactless Card Reader w/Keypad | Ea | 2006 Price List | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13851-065-1010. Labor hours multiplied by 2006 electrician rate | N/A
(HID Prox Pro - 5355)
Fingerprint Reader | Ea | Phone Call to Manufacturer | Estimated | N/A
(Bioscrypt V-Smart-A-H)
Proximity Cards | Ea | 2005 ADI Price List, Pg 23 | N/A | N/A
(HID ISOProx II-1386LGGSN)
Smart Cards | Ea | 2005 ADI Price List, Pg 23 | N/A | N/A
(HID iClass-2002PGGMN)
Card Reader Stanchion | Ea | Phone call to Manufacturer, dealer pricing 1.800.377.4636 | Estimated | N/A
(Engineered Parking Systems 306-4)
Concrete Pad for Stanchion | CY | 2006 RS Means, Pg 103, row 03310-240-3800 | 2006 RS Means, Pg 103, row 03310-240-3800 | 2006 RS Means, Pg 103, row 03310-240-3800
(Generic-2' x 2' x 1')
Balanced Magnetic Switch | Ea | 2005 ADI Price List, Pg 20 | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13851-065-1400. Labor hours multiplied by 2006 electrician rate | N/A
(GE 1076D)
High Security Balanced Magnetic Switch | Ea | 2005 ADI Catalog, Pg 42 | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13851-065-1400. Labor hours multiplied by 2006 electrician rate | N/A
(GE SR-2707A)
Request-to-Exit Motion Sensor | Ea | 2005 ADI Price List, Pg 11 | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13851-065-3200. Labor hours multiplied by 2006 electrician rate | N/A
(Detection Systems 150i)
Magnetic Lock | Ea | 2005 ADI Price List, Pg 40 | Phone call to local supplier. OESCO Infosys | N/A
(Locknetics 390 Plus)
Request-to-Exit Push Button | Ea | 2005 ADI Catalog, Pg 183 | Phone call to local supplier. OESCO Infosys | N/A
(Securitron SN-PB5)
Interior 360-Degree Motion Detector D/T | Ea | Phone call to Manufacturer. List pricing | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13851-065-2800. Labor hours multiplied by 2006 electrician rate | N/A
(Detection Systems DS-9370)
Exterior Dual Technology Motion Detector | Ea | Phone call to Manufacturer. Dealer pricing | Staff experience | N/A
(Protech USA SDI-77XL-MIL)
Interior Fixed Camera | Ea | 2005 Pelco Price List, Dealer pricing, pg 3 | 2006 RS Means, Building Construction Cost Data, Pg. 499, row 16850-600-2400 | N/A
(Pelco ICS150-CDV4A)
Exterior PTZ Camera | Ea | 2005 Manufacturer's Price List, Dealer pricing, Index pg 48 | Staff experience | N/A
(Pelco Spectra III SE-SD53CBW-PG-E1)
Thermal Imaging PTZ Camera | Ea | Phone Call and Quote from Manufacturer. EMX. Chris Canter. | Staff experience | N/A
(EMX 8000/2X)
Exterior PTZ Camera Wall Mount | Ea | 2005 Manufacturer's Price List, Dealer pricing, Index pg 47 | Staff experience | N/A
(Pelco MRWA)
Video Analytics Processor | Ea | Quote from Manufacturer | Quote from Manufacturer | N/A
(Guardian Solutions)
Video Analytics Software | Ea | Quote from Manufacturer | N/A | N/A
(Guardian Solutions)
Camera Calibration | Ea | N/A | Quote from Manufacturer | N/A
(Guardian Solutions)
Best Practices/Procedures Training | Ea | N/A | Quote from Manufacturer | N/A
(Guardian Solutions)
Server for Analytic Software | Ea | Quote from Manufacturer | Quote from Manufacturer | N/A
(Generic)
Exterior PTZ Camera Pole Mount | Ea | 2005 Manufacturer's Price List, Dealer pricing, pg 13 | Staff experience | N/A
(Pelco PP350)
Matrix Switcher | Ea | 2005 Manufacturer's Price List, dealer pricing, pg 5 | Staff experience | N/A
(Pelco CM6700, CM9760-CDU-T, PV130)
Keyboard Controller | Ea | 2005 Manufacturer's Price List, dealer pricing, pg 44 | Staff experience | N/A
(Pelco KBD300A)
Fiber Video Transmitter/Multiplexer | Ea | Quote from Manufacturer | Staff experience | N/A
(IFS VT6010DRDT and VR6010DRDT)
Fiber Data Transceiver | Ea | Quote from Manufacturer | Staff experience | N/A
(IFS D1010)
Panel and Power Supply | Ea | 2004 Manufacturer's MSRP List, Row 922, discounted 25% | Staff experience | N/A
(Lenel LNL-OLS75CTX)
Panel and Power Supply | Ea | 2004 Manufacturer's MSRP List, Row 919, discounted 25% | Staff experience | N/A
(Lenel LNL-OLS120CTX)
Battery Back-Up for ACS Panel | Ea | 2004 Manufacturer's MSRP List, Row 141, discounted 25% | Staff experience | N/A
(Lenel ABT-12)
Ethernet Module to Connect to LAN | Ea | 2004 Manufacturer's MSRP List, Row 916, discounted 25% | Staff experience | N/A
(Lenel LNL-ETHLAN)
Ethernet Cable | Ea | Generic | Staff experience | N/A
(Generic)
System Controller | Ea | 2004 Manufacturer's MSRP List, Row 867, discounted 25% | Staff experience | N/A
(Lenel LNL-1000)
Single Card Reader Module | Ea | 2004 Manufacturer's MSRP List, Row 875, discounted 25% | Staff experience | N/A
(Lenel LNL-1300)
Input Control Module | Ea | 2004 Manufacturer's MSRP List, Row 873, discounted 25% | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13850-065-2800. Labor hours multiplied by 2006 electrician rate | N/A
(Lenel LNL-1100)
Power Supply for Door Hardware | Ea | 2005 ADI Price List, Pg 51 | 2003 RS Means, Building Security Strategies and Costs, Pg 245, row 13700-300-0380. Labor hours multiplied by 2006 electrician rate | N/A
(SDC SZ-602RF)
ACS Workstation | Ea | 2004 Manufacturer's MSRP List, Row 1201, 378, 1188, 1458, discounted 25% | Staff Experience | N/A
(Lenel PCC-32ESI, CAM500-KUSB, P210)
Camera Power Supply and Enclosure | Ea | 2005 Manufacturer's Price List, Dealer pricing, pg 59 | Staff Experience | N/A
(Pelco MCS4-2)
Camera Power Supply and Enclosure | Ea | 2005 Manufacturer's Price List, Dealer pricing, pg 59 | Staff Experience | N/A
(Pelco MCS16-20)
Camera Power Supply and Enclosure | Ea | 2005 Manufacturer's Price List, Dealer pricing, pg 59 | Staff Experience | N/A
(Pelco WCS1-4)
Digital Video Recorder (600 GbHD) | Ea | 2004 Manufacturer's MSRP List, Row 655, 622 discounted 25% | Staff Experience | N/A
(Lenel DVS-16-S)
17" Flat Screen LCD Monitor | Ea | 2005 ADI Catalog, Pg 130 | Staff Experience | N/A
(Bosch MON171CL)
Uninterruptible Power Supply | Ea | Internet, MSRP discounted 25% | Staff Experience | N/A
(Powerware 9125 2000)
Equipment Rack | Ea | Previous Project | Staff Experience | N/A
(Middle Atlantic -VRK-44-31H, MW-LVT, etc)
Wiring 18-2c | Lf | Manufacturer's price quote | 2006 RS Means, Pg 475, row 16120-280-0020 | N/A
(CSC 151000)
Wiring 18-4c | Lf | Manufacturer's price quote | 2006 RS Means, Pg 475, row 16120-280-0020 | N/A
(CSC 151200)
Wiring 18-6c | Lf | Manufacturer's price quote | 2006 RS Means, Pg 475, row 16120-280-0020 | N/A
(CSC 151230)
Coaxial/Power Cable RG59U with 18/2c | Ea | Manufacturer's price quote | 2006 RS Means, Pg 475, row 16120-280-0020 | N/A
(CSC 516681)
20' Wooden Pole | Ls | 2003 Building Security Strategies and Costs, pg 321, line 2920. Cost less fixture and lamp, plus 5% per year inflation | 2003 Building Security Strategies and Costs, pg 321, line 2920. Cost less fixture and lamp, plus 5% per year inflation | N/A
(Generic-incl base, excavation, fill, etc)
3" Galvanized Pole for Motion Detector | Ea | 2006 RS Means, Pg 65, row 02820-130-1100 | 2006 RS Means, Pg 65, row 02820-130-1100 | 2006 RS Means, Pg 65, row 02820-130-1100
(Generic)
Trenching and Backfill | Lf | 2006 RS Means, Pg 41, row 02315-620-100 and 1050 | 2006 RS Means, Pg 41, row 02315-620-100 and 1050 | 2006 RS Means, Pg 41, row 02315-620-100 and 1050
(Generic)
Sod Removal and Install | Ls | 2006 RS Means, Pg 76, row 02910-720-4100 and row 02920-400-0300 | 2006 RS Means, Pg 76, row 02910-720-4100 and row 02920-400-0300 | 2006 RS Means, Pg 76, row 02910-720-4100 and row 02920-400-0300
(Generic)
6" x 6" NEMA 4 Enclosure | Ea | 2006 RS Means, Pg 481, row 16136-700-3050 | 2006 RS Means, Pg 481, row 16136-700-3050 | N/A
(Generic)
24" x 24" NEMA 4 Enclosure | Ea | 2006 RS Means, Pg 478, row 16136-700-3400 | 2006 RS Means, Pg 478, row 16136-700-3400 | N/A
(Generic)
3/4" Rigid Galvanized Conduit | Ea | 2006 RS Means, Pg 478, row 16132-205-1770 | 2006 RS Means, Pg 478, row 16132-205-1770 | N/A
(Generic)
1/2/" Rigid Galvanized Conduit | Ea | 2006 RS Means, Pg 478, row 16132-205-1750 | 2006 RS Means, Pg 478, row 16132-205-1750 | N/A
(Generic)
\
120 Volt Drop | Ls | 2006 RS Mean, Pg 478, row 16132-205-1750, Pg 477, row 16120-900-0940, pg 484, row 16139-700-4015 | 2006 RS Mean, Pg 478, row 16132-205-1750, Pg 477, row 16120-900-0940, pg 484, row 16139-700-4015 | N/A
(Generic)