## 1. Instructions
VA FM Data Spreadsheet - v1.0
1.0 Purpose
Table 13 and 23 data requirements identified in this spreadsheet will be integrated into the VA's MAXIMO Facility Management program. All data applicable to the specific project shall comply
with this standard. For more information on required standards including data deliverables see The VA BIM Manual and project contractual scope.
Documents Referenced
• VA BIM Manual v2.0 - November 2016
• A/E Submission Requirements for VA Medical Center Major New Facilities, Additions & Revisions, Program Guide PG 18-15 Volume B
• OmniClass Table 13 - Spaces by Function - National Standard - May 16, 2012
• OmniClass Table 23 - Spaces by Function - National Standard - May 16, 2012
2.0 OmniClass Table 13 Space by Function Data Requirements
1. For all project applicable spaces, (VA) Owner, (AE) Arch/Eng, or (GC) Constructor is to provide the identified data in Table 13 Space Attribute Scope.
2. Note that data categories identified with "+" sign have extended data attribute requirements (i.e. Basic_Object+ - includes nine separate data attributes).
3. Table 13 Space Attribute Definition provides a breakdown on the individual attributes, data types, Unit of Measure, COBie/Maximo identifier, deliverable type, description, and contractual ownership.
4. Under the Table 13 Space Attribute Definition column "COBie/Column": if the Field is blank then the (VA) Owner, (AE) Arch/Eng, or (GC) Constructor shall provide a COBie attribute using the "Maximo" Field Identifier.
5. Minimal deliverable of data will include an IFC and COBie format electronic file in the latest version available at the time of the project completition. See VA BIM Standards for detailed requirements.
6. Where level 1 (i.e. Item #7, 12-23 00 00) OmniClass space identifies data requirements (as shown below):
a) The (VA) Owner, (AE) Arch/Eng, or (GC) Constructor must provide data for all spaces identified under OmniClass table 13 (Not all spaces are shown in table)
b) or provide data for specific spaces where the requirement varies as shown under 13-23-11 13 11.
3.0 OmniClass Table 23 Product Data Requirements
1. For all project applicable Elements, the (VA) Owner, (AE) Arch/Eng, or (GC) Constructor is to provide the identified data in Table 23 Asset Attribute Scope.
2. Note that data categories identified with "+" sign have extended data attribute requirements (i.e. Basic_Object+ - includes seven separate data attributes).
3. Table 23 Asset Attribute Definition provides a breakdown on the individual attributes, data types, Unit of Measure, COBie/Maximo identifier, deliverable type, description, and contractual ownership.
4. Under the Table 23 Asset Attribute Definition column "COBie/Column": if the Field is blank then the (VA) Owner, (AE) Arch/Eng, or (GC) Constructor shall provide a COBie attribute using the "Maximo" Field Identifier.
5. Minimal deliverable of data will include an IFC and COBie format electronic file in the latest version available at the time of the project completition. See VA BIM Standardsl for detailed requirements.
6. Some Data "+" groups were shown expanded due to variances in the data requirement.
a) All attributes apply to data "+" categories that are not shown expanded (i.e. Condition+).
b) Whereas "Operating+" is expanded due to specific attribute requirement for individual products listed.
4.0 COBie Columns noted "MAXIMO ID"
Fields noted "SEE INSTRUCTIONS" are attributes not identified under the Cobie Column of the COBieData Field Name . These attributes will be identified using the "Maximo ID" under the
Name column of the "Attribute" COBie tab as shown below. This applies to both "2.2 Space Attribute Definition" and "3.2 Asset Attribute Definition" tables
5.0 LIST OF MAJOR CONTRIBUTERS TO VA'S FM STANDARD
ORGANIZATION - OWNER/CONSULTING FIRM - CONSULTANT
• JKN Solutions – Malcolm Junkin
• VA Palo Alto Healthcare System – Stephen G. McGrath, Supervisory Engineer
• HDR – Dennis Patnode
• EcoDomus – Igor Starkov
• Onuma Inc – Kimon Onuma
• Fallon Associates Inc. – Kristine Fallon, Danielle Gran
• USACE – Steve Hutsell, Van Woods, and USACE/Industry BIM and CIM Consortia (UIBCC)
• Walsh Construction – Steve Cook
6.0 DOCUMENT REVISION HISTORY TABLE
ITEM# | VERSION RELEASE# | REVISION DATE |  | REVISION DESCRIPTION | REVISION NOTES
1 | V1.0 | 2016-11-10 | First release of VA FM Standard
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19

## 2.1 Space Attribute Scope
|  |  |  | VA BIM STANDARD OmniClass Table 13 Space Attribute Scope - v1.0 | [16 empty] | 13
|  | OmniClass | Description | [7 empty] | Attribute Groups | [8 empty] | Definition
Item Number | OmniClass Level |  |  | Basic Object + | Functional Use | Criticality | Security Level | Condition + | SEPS Dept. | Area + | Capacity + | Size + | Flooring + | Walls + | Ceiling + | Lighting + | Red Power + | Environment + | Med Gas +
1 | 1 | 13-15 00 00 | Wall Spaces
2 | 2 | 13-15 11 00 | Exterior Wall Space | • | • |  |  |  | • | • | [5 empty] | • |  |  |  | The space of a wall that divides/separates inside spaces from outside spaces. The wall may be structural or non-structural
3 | 2 | 13-15 13 00 | Interior Wall Space | • | • |  |  |  | • | • | [9 empty] | The space of a wall that divides/separates inside spaces only. The wall may be structural or non-structural
4 | 1 | 13-21 00 00 | Parking Spaces
5 | 2 | 13-21 11 00 | Exterior Parking Spaces | • | • |  |  |  | • | • | • |  |  |  |  | • |  |  |  | Outdoor area used for transient storage of motor vehicles, not including loading docks, sally ports and building service areas such as enclosed auxiliary lobbies used to enter a building from parking areas.
6 | 2 | 13-21 13 00 | Interior Parking Spaces | • | • |  |  |  | • | • | • |  |  |  |  | • |  |  |  | Totally or partially enclosed space that is normally used to circulate and station vehicles.
7 | 1 | 13-23 00 00 | Facility Service Spaces | • | • |  |  |  | • | • | • | • | • | • | • | •
8 | 4 | 13-23 11 11 11 | Elevator Shaft | • | • |  |  |  |  | • | • | • | [7 empty] | An enclosed space extending through one or more stories of a building connecting vertical openings in successive floors, or floors and the roof used to enclose an elevator.
9 | 4 | 13-23 11 11 21 | Escalator | • | • |  |  |  |  | • | • | • |  |  |  | • |  |  |  | Set of moving steps attached to a continuously circulating belt that carries people up or down between levels in a building.
10 | 4 | 13-23 11 13 11 | Egress Stairway | • | • |  |  |  |  | • | • | • | • | • | • | • |  |  |  | A stair that is part of an exit or leads to an exit.
11 | 3 | 13-23 11 17 | Ramp | • | • |  |  |  |  | • | • | • | • | • |  | • |  |  |  | A walking surface that has a running slope steeper than 1 unit vertical in 20 units horizontal (5-percent slope). (IBC)
12 | 3 | 13-23 11 21 | Chute | • | • |  |  |  | • | • | • | • |  | • | [5 empty] | (postal, refuse, laundry) which end at a "termination room" - a shaft enclosure that does not extend to the underside of the roof sheathing, deck, or slab of the building.
13 | 3 | 13-23 11 23 | Service Riser Space | • | • |  |  |  |  | • | • | • |  | • | [5 empty] | Space used to accommodate intra-floor services such as flues, fire towers, fire hose cabinets (because of the pipes attached to them), stacks, pipe shafts, electricity, vertical air conditioning ducts and other vertical ducts.
14 | 2 | 13-23 12 00 | Horizontal Infrastructure/Service Space, Non-Occupied | • | • |  |  |  |  | • | • | • |  |  | • |  |  |  |  | Space solely used to accommodate horizontal distribution of infrastructure for HVAC, Power and Communications. Within Interstitial space the tracking of horizontal distribution is optional. Generally the final distribution such as electrical circuits within an office area are not tracked.
15 | 3 | 13-23 13 11 | Fire Command Center | • | • | • |  |  | • | • |  |  | • | • | • | • |  |  |  | Space for fire department operations with the location, layout, content and features and approved by the fire department; includes Fire Protection System (FPS)
16 | 3 | 13-23 13 13 | Guard Stations | • | • | • | • |  | • | • | • |  | • | • | • | • |  |  |  | Booth or room within building line used to house security for building or tenant.
17 | 2 | 13-23 17 00 | Restroom | • | • |  |  |  |  | • | • |  | • | • | • | • |  |  |  | A space with washing and toilet facilities.
18 | 2 | 13-23 19 00 | Utility Equipment Room | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Space provided for the general operation of heating, ventilating, and air conditioning, plumbing and electrical, life safety and communication services; including sections of tunnels which are dedicated to distribution of utilities.
19 | 2 | 13-23 21 00 | Waste and Recycling Spaces | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Space used for holding garbage and recyclable materials.
20 | 3 | 13-23 21 11 | Hazardous Waste Storage | • | • | • |  |  | • | • |  |  | • | • | • | • |  | • |  | An area used for the storage of chemicals or substances that pose a physical or health hazard that are in waste condition.
21 | 3 | 13-23 23 13 | Custodial Space | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Room that contains sink(s) or mop sink(s) and is used by custodial services for CUST. their related activities.
22 | 3 | 13-23 23 15 | Shop Area | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | A place where things are crafted
23 | 1 | 13-25 00 00 | Circulation Spaces
24 | 3 | 13-25 11 11 | Corridor | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | An enclosed exit access component that defines and provides a path of egress travel to an exit.
25 | 3 | 13-25 13 13 | Entry Lobby | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | A large entrance area of hall that serves as a foyer
26 | 3 | 13-25 13 19 | Elevator Lobby | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | Lobby that separates the elevator shaft enclosure doors from each floor by fire partitions.
27 | 1 | 13-31 00 00 | Education and Training Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Space used for education.
28 | 1 | 13-33 00 00 | Recreation Spaces
29 | 2 | 13-33 11 00 | Athletic Recreation Spaces | • | • |  |  |  | • | • | [5 empty] | • |  |  |  | Spaces for participating in sports and athletic activities.
30 | 2 | 13-33 13 00 | Swimming Pools | • | • |  |  |  | • | • |  | • |  |  |  | •
31 | 2 | 13-33 15 00 | Non-Athletic Recreation Spaces | • | • |  |  |  | • | • | [5 empty] | • |  |  |  | Spaces for recreation and entertainment that do not include athletic activity or sports.
32 | 3 | 13-33 17 11 | Fitness Center | • | • |  |  |  | • | • | • | • | • | • | • | • |  |  |  | Spaces for exercise and fitness activities.
33 | 1 | 13-41 00 00 | Museum Spaces | • | • |  |  |  | • | • |  |  | • | • | • | •
34 | 1 | 13-45 00 00 | Library Spaces | • | • |  |  |  | • | • | • |  | • | • | • | •
35 | 1 | 13-47 11 00 | Worship spaces | • | • |  |  |  | • | • | • | • | • | • | • | • |  |  |  | Spaces for conducting worship activities, such as prayer, religious or spiritual ceremonies or celebration, or meditation.
36 | 2 | 13-47 17 00 | Death Spaces | • | • |  | • |  | • | • | • |  | • | • | • | • |  |  |  | Spaces for religious and other proceedings surrounding death, funerals, and internment.
37 | 1 | 13-51 00 00 | Healthcare Spaces
38 | 2 | 13-51 11 00 | General Examination Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Spaces used by multiple medical services for routine patient examinations.
39 | 3 | 13-51 14 19 | Labor, Delivery, Recovery, Postpartum Room | • | • |  |  |  | • | • | • |  | • | • | • | • | • | • | • | Space used for the “birthing process” including pre-delivery preparation, delivery, and post delivery recovery. Where the acronym is “LDR” the function does not include the post recovery hospital stay for the mother.
40 | 3 | 13-51 14 33 | Nursery, Special Care | • | • |  |  |  | • | • | • |  | • | • | • | • | • | • | • | Space used for observation of newborn infants prior to placement in a newborn nursery or when their condition requires heightened attention or special intervention.
41 | 3 | 13-51 14 35 | Patient Room | • | • | • | • |  | • | • | • |  | • | • | • | • | • | • | • | Space used for overnight patient care.
42 | 3 | 13-51 17 17 | Consultation Room, Patient | • | • |  |  |  | • | • | • |  | • | • | • | • | • |  |  | Space used for meetings with patients and family members to discuss health status, learn health history, and provide information.
43 | 3 | 13-51 17 21 | Equipment Storage Room, Healthcare | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Space used for storage of equipment such as surgical tables, accessories, carts, etc.
44 | 3 | 13-51 17 22 | Medical Records Storage Room | • | • |  | • |  | • | • | • |  | • | • | • | • |  |  |  | Space used for organized, active filing of physical patient charts, in a specially ordered and controlled environment
45 | 3 | 13-51 17 23 | Nurse Workspaces | • | • |  |  |  | • |  |  | • |  |  |  | • |  |  |  | Spaces used by nurses to perform their work and administer activities.
46 | 3 | 13-51 17 27 | Soiled Utility/Supply Room, Healthcare | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Space used for clean up of equipment Space used for patient care, disposal of trash and biologic waste and storage of soiled linen.
47 | 2 | 13-51 21 00 | Diagnostic Imaging Spaces | • | • | • | • |  | • | • |  | • | • | • | • | • | • | • | • | Spaces used for examination of patients by devices which produce an image of tissue, bone, or biophysical structure excluding those used in cardiac diagnostic and interventional services, nuclear medicine services, and radiation therapy services.
48 | 2 | 13-51 24 00 | Diagnostic Imaging Support Spaces | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | Spaces used in support of imaging equipment and personnel.
49 | 2 | 13-51 27 00 | Radiation Diagnostic and Therapy Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • | • |  |  | Spaces used for examination and treatment of patients by devices which primarily use ionizing radiation or its byproducts (such as thallium). This section is limited to systems used for oncology and nuclear medicine.
50 | 2 | 13-51 31 00 | Heart and Lung Diagnostic and Treatment Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • | • |  |  | Spaces used for cardiac and pulmonary function diagnostic and interventional services.
51 | 3 | 13-51 31 37 | Procedure Viewing Area | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Space used for observation of invasive cardiology procedures done in a catheterization laboratory.
52 | 2 | 13-51 34 00 | General Diagnostic Procedure and Treatment Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • | • |  |  | Spaces used by multiple medical services for specific diagnostic and treatment functions which are typically exclusive to those services.
53 | 2 | 13-51 37 00 | Eye and Ear Healthcare Spaces | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Spaces used for diagnosis and treatment of conditions relating to sight, hearing, balance and related functions.
54 | 2 | 13-51 41 00 | Endoscopy/Gastroenterology Spaces | • | • |  |  |  | • | • |  |  | • | • | • | • | • | • |  | Spaces used for examinations and treatments of the esophagus, lungs, stomach, digestive and associated anatomical structures using endoscopes and related systems.
55 | 2 | 13-51 44 00 | Surgical Spaces | • | • | • | • |  | • | • | • | • | • | • | • | • | • | • | • | Spaces used for surgical procedures and for direct support of surgical functions.
56 | 2 | 13-51 47 00 | Clinical Laboratory Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • |  | • |  | Spaces used for testing of human biological specimens to determine health status, to diagnose disease, and to prepare blood and serum for patient use.
57 | 3 | 13-51 51 00 | Clinical Laboratory Support Spaces | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | Spaces used exclusively in support of clinical laboratory operations.
58 | 3 | 13-51 51 19 | Blood Specimen Collection Room | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Space used for phlebotomy, drawing of blood specimens from patients.
59 | 2 | 13-51 54 00 | Pharmacy Spaces | • | • |  | • |  | • | • |  |  | • | • | • | • |  | • |  | Spaces used to receive, prepare, compound, test and examine pharmaceuticals and to dispense them as requested for patient care.
60 | 2 | 13-51 57 00 | Medical Services Logistic Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • |  |  |  | Spaces used for cleaning, sterilizing, packaging, stocking and distributing various types of supplies in a health care setting. Includes spaces used for receiving and holding soiled linens and receiving and distributing clean linens.
61 | 3 | 13-51 57 25 | Clean Supply Preparation Area, Healthcare | • | • |  |  |  | • | • |  | • | • | • | • | • |  | • |  | Space used for equipment and supply packaging and preparation for future use where storage is provided elsewhere.
62 | 2 | 13-51 61 00 | Rehabilitation Spaces | • | • |  |  |  | • | • | • | • | • | • | • | • |  |  |  | Spaces used for physical and occupational/vocational rehabilitation, for designing, and for manufacturing dispensing and fitting orthotic and prosthetic appliances.
63 | 2 | 13-51 64 00 | Dental Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • | • |  | • | Spaces used for dental hygiene care, routine dentistry, and for design, fabrication, application and adjustment of dental and maxillo-facial appliances for corrective and reconstructive purposes.
64 | 2 | 13-51 67 00 | Medical Research and Development Spaces | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | Spaces used for basic research on the nature and prevention of disease and injury. May involve use of animals and/or highly toxic or infectious matter which must be contained in special rooms or suites of rooms.
65 | 3 | 13-51 91 00 | Veterinary Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • |  | • |  | Spaces used for housing, treatment, training and other types of care for animals.
67 | 1 | 13-55 11 00 | Office Spaces | • | • |  |  |  | • | • |  |  | • | • | • | • |  |  |  | Space in which business, clerical or professional activities are conducted.
68 |  | 13-55 29 15 | Post Office Space | • | • |  | • |  | • | • |  |  | • | • | • | • |  |  |  | Specialized space in a facility that houses United States Postal Service operations.
69 |  | 13-55 29 17 | Mail Room Space | • | • |  | • |  | • | • | • |  | • | • | • | • |  |  |  | Mail sorting and distribution space including remote mail stops on floors.
70 |  | 13-55 29 21 11 | Conference Room | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Any office room used primarily as a conference room by a single tenant
71 | 1 | 13-57 00 00 | Service Activity Spaces
72 |  | 13-57 13 00 | Food Service | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Space used for preparation and serving of food or providing seating for dining.
73 |  | 13-57 15 00 | Child Care Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Spaces designed for the care of a young child or children
74 |  | 13-57 17 13 | Break Room | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | A room at a business which is set aside for coffee breaks, snacks, lunches, etc. Synonym: Lunchroom
78 | 1 | 13-63 00 00 | Storage Spaces
79 |  | 13-63 11 00 | Warehouse Spaces | • | • |  | • |  | • | • | • | • | • | • | • | • |  |  |  | Space specifically designed for the storage of raw material, in process materials or finished goods.
80 |  | 13-63 13 00 | Non-Warehouse Storage Spaces | • | • |  |  |  | • | • |  | • | • | • | • | • |  |  |  | Spaces for the storage of goods and materials for long and short terms
81 |  | 13-63 17 11 | Refrigeration Compartment | • | • | • |  |  | • | • | • | • | • | • | • | • |  | • |  | Space served by refrigeration equipment, used to lower the internal temperature, often for the purposes of storing perishables.
82 |  | 13-63 17 13 | Freezing Compartment | • | • | • |  |  | • | • | • | • | • | • | • | • |  | • |  | Space served by equipment to lower the internal temperature below the freezing point of water, often for the purposes of storing perishables.
83 | 1 | 13-65 00 00 | Private Residential Spaces | • | • |  |  |  | • | • | • |  | • | • | • | • |  |  |  | Space used to provide accommodation for people when not at work. The accommodation provides facilities for sleeping and relaxation and usually cooking, eating, and cleaning.
85 | 1 | 13-69 00 00 | Building Associated Spaces
86 | 2 | 13-69 11 00 | Roof | • | • |  | • |  |  | • |  |  | • |  |  | • |  |  |  | A construct oriented more than 15º from vertical that Encloses the interior of a Building underneath from the exterior above, affording protection from the elements appropriate to the occupancy and the local climate.
87 | 2 | 13-69 25 00 | Pedestrian Travel Spaces | • | • |  |  |  |  | • | [5 empty] | • |  |  |  | Spaces for travel by people on foot.

## 2.2 Space Attribute Definitiion
|  |  | VA BIM STANDARD OmniClass Table 13 Space Attribute Definitions - v1.0 | [6 empty] | 13
Item Number | Attribute Group | Attribute | Data Type | Unit of Measure | COBie Data Field Name |  | Maximo ID | Provided By (VA) Owner | Deliverable Type | Definition
[5 empty] | COBie Tab | COBie Column |  | (AE) Arch/Eng (GC) Constructor
1 | Basic_Object + | Identifier | Text | N/A | Attribute | "MAXIMO ID" | LOCATIONSID | AE | COBie | Free text space identifier
2 |  | Name | Text | N/A | Space | Name | VA_ROOM | AE | COBie | Free text name of space
3 |  | OmniClass_Category | Number | N/A | Space | Category | VA_OMNI_14 | AE | COBie | Form use category based on OmniClass Table 14
4 |  | Parent | Number | N/A | Attribute | "MAXIMO ID" | LOCHIERARCHY.PARENT | AE | COBie | Next up LOCATIONSID in Hierarchy - VA_ROOM, VA_FLOOR, VA_WING, VA_BUILDING, VA_CAMPUS
5 |  | Location | Text | N/A | Facility | SiteName | LOCATION | AE | COBie | Free text further description of space name
6 |  | Description | Text | N/A | Space | Description | DESCRIPTION | AE | COBie | Free text further description of space
7 |  | Bar_Code | Alphanumeric Number | N/A | Component | BarCode | VA_BAR_CODE | VA | COBie | Identification bar code. NOT data bar code.
|  | GUID | Text | N/A | Attribute |  |  | GC | COBie | External ID
8 |  | Installed_Date | YYYY-MM-DD | Date | Component | InstallationDate | VA_INSTALLED_DATE | GC | COBie | Date placed in service (beneficial occupancy date).
9 |  | Installed_Cost | Number | $US | Attribute | "MAXIMO ID" | VA_INSTALLED_COST | GC | COBie | Estimated cost of labor and materials. Normally at the building level.
10 | Functional Use | OmniClass_Functional_Use | Text | N/A | Attribute | "MAXIMO ID" | VA_OMNI_13 | AE | COBie | Functional use category based on OmniClass Table 13
11 | Criticality | Criticality | Text | N/A | Attribute | "MAXIMO ID" | VA_CRITICALITY | VA | COBie | VA designated Criticality code from domain list (pick list).
12 | Security Level | Security_Level | Number | N/A | Attribute | "MAXIMO ID" | SECURITY_LEVEL | VA | COBie | VA designated Security Level code from domain list.
13 | Condition + | Condition_Assessment | Number | N/A | Attribute | "MAXIMO ID" | CONDITION_ASSESSMENT | VA | COBie | VA designated Condition Assessment Code from domain list. Eventually may be computational from multiple field algorithm.
14 |  | Condition_Assessment_Date | YYYY-MM-DD | Date | Attribute | "MAXIMO ID" | CONDITION_ASSESSMENT_DATE | VA | COBie | Date of the recorded Condition Assessment
15 | SEPS Dept | Department | Number | Dept. | Attribute | "MAXIMO ID" | DEPARTMENT | VA | COBie | Use Department (Chapter) from SEPS
16 | Area + | Net_Area | Number | SqFt | Space | NetArea | VA_AREA_NET | AE | COBie | Net area … inside locations
17 |  | Gross_Area | Number | SqFt | Space | GrossArea | VA_AREA_SQFT | AE | COBie | Gross, where applicable based on VA guidance (e.g. at building level)
18 | Capacity + | Capacity | Number | Specified | Attribute | "MAXIMO ID" | CAPACITY | AE | COBie | Current configuration or utilization.
19 |  | Maximum Capacity | Number | Specified | Attribute | "MAXIMO ID" | MAX_CAPACITY | AE | COBie | Maximum configuration or utilization.
20 |  | Capacity Unit of Measure | Text | N/A | Attribute | "MAXIMO ID" | CAPACITY_UM |  |  | Companion Capacity Unit of Measure … occupants, seats, beds, etc.
21 | Size + | Height | Number | Feet | Attribute | "MAXIMO ID" | HEIGHT | AE | COBie | Nominal height if not uniform
22 |  | Length | Number | Feet | Attribute | "MAXIMO ID" | LENGTH | AE | COBie | Nominal length if not rectangular
23 |  | Width | Number | Feet | Attribute | "MAXIMO ID" | WIDTH | AE | COBie | Nominal width if not rectangular
24 |  | Volume | Number | CuFt | Attribute | "MAXIMO ID" | VOLUME | AE | COBie | L x W x H unless not uniform dimensions
25 | Floors + | Material | Text | N/A | Attribute | "MAXIMO ID" | FLOOR_MATERIAL | AE | COBie | Predominant floor surface material
26 |  | Finish | Text | N/A | Attribute | "MAXIMO ID" | FLOOR_FINISH | AE | COBie | Predominant floor surface finish
27 |  | Color | Text | N/A | Attribute | "MAXIMO ID" | FLOOR_COLOR | AE | COBie | Predominant floor color
28 |  | Fire Rating | Number | Hours | Attribute | "MAXIMO ID" | FLOOR_FIRE_RATING | AE | COBie | Floor fire rating in hours
29 |  | Load Rating | Number | PSF | Attribute | "MAXIMO ID" | FLOOR_LOAD_RATING | AE | COBie | Average load rating for floor in PSF
30 |  | Blast Rating | Number | PSI/T | Attribute | "MAXIMO ID" | FLOOR_BLAST_RATING | AE | COBie | Floor blast rating in PSI/T
31 |  | Penetrations | Number | Ea | Attribute | "MAXIMO ID" | FLOOR_PENETRATIONS | AE | COBie | Number of penetrations in floor
32 | Walls + | Material | Text | N/A | Attribute | "MAXIMO ID" | WALLS_MATERIAL | AE | COBie | Predominant wall subsurface material
33 |  | Finish | Text | N/A | Attribute | "MAXIMO ID" | WALLS_FINISH | AE | COBie | Predominant wall finish
34 |  | Color | Text | N/A | Attribute | "MAXIMO ID" | WALLS_COLOR | AE | COBie | Predominant wall color
35 |  | Fire_Rating | Number | Hours | Attribute | "MAXIMO ID" | WALLS_FIRE_RATING | AE | COBie | Wall fire rating in hours
36 |  | Blast_Rating | Number | PSI/T | Attribute | "MAXIMO ID" | WALLS_BLAST_RATING | AE | COBie | Wall blast rating in PSI/T
37 |  | Penetrations | Number | Ea | Attribute | "MAXIMO ID" | WALLS_PENETRATIONS | AE | COBie | Number of penetrations in walls, excluding doors
38 | Ceiling + | Material | Text | N/A | Attribute | "MAXIMO ID" | CEILING_MATERIAL | AE | COBie | Predominant ceiling subsurface material
39 |  | Finish | Text | N/A | Attribute | "MAXIMO ID" | CEILING_FINISH | AE | COBie | Predominant ceiling finish
40 |  | Color | Text | N/A | Attribute | "MAXIMO ID" | CEILING_COLOR | AE | COBie | Predominant ceiling color
41 |  | Fire_Rating | Number | Hours | Attribute | "MAXIMO ID" | CEILING_FIRE_RATING | AE | COBie | Ceiling fire rating in hours
42 |  | Load_Rating | Number | PSF | Attribute | "MAXIMO ID" | CEILING_LOAD_RATING | AE | COBie | Average load rating for ceiling in PSF
43 |  | Blast_Rating | Number | PSI/T | Attribute | "MAXIMO ID" | CEILING_BLAST_RATING | AE | COBie | Ceiling blast rating in PSI/T
44 |  | Penetrations | Number | Ea | Attribute | "MAXIMO ID" | CEILING_PENETRATIONS | AE | COBie | Number of penetrations in ceiling
45 | Lighting + | Type | Text | N/A | Attribute | "MAXIMO ID" | LIGHTING_TYPE | AE | COBie | Predominant lighting type (Incandescent, fluorescent, LED, etc.)
46 |  | Fixtures | Number | Ea | Attribute | "MAXIMO ID" | FIXTURES | AE | COBie | Total number of fixtures (Predominant and other)
47 |  | Luminosity | Number | FC | Attribute | "MAXIMO ID" | LUMINOSITY | AE | COBie | Luminosity of predominant fixtures
48 |  | Emergency Type | Text | N/A | Attribute | "MAXIMO ID" | EMERGENCY_TYPE | AE | COBie | Type if present
49 |  | Emergency Fixtures | Number | Ea | Attribute | "MAXIMO ID" | EMERGENCY_FIXTURES | AE | COBie | Number of emergency fixtures
50 | Red Power + | Critical_Branch_110/120_Outlets | Number | Ea | Attribute | "MAXIMO ID" | RED_CRITICAL_110_120_OUTLETS | AE | COBie | Red power critical branch 110/120v outlets
51 |  | Critical_Branch_208_Outlets | Number | Ea | Attribute | "MAXIMO ID" | RED_CRITICAL_208_OUTLETS | AE | COBie | Red power critical branch 208v outlets
52 |  | Equipment_Branch_110/120_Outlets | Number | Ea | Attribute | "MAXIMO ID" | RED_EQUIP_110_120_OUTLETS | AE | COBie | Red power equipment branch 110/120v outlets
53 |  | Equipment_Branch_208_Outlets | Number | Ea | Attribute | "MAXIMO ID" | RED_EQUIP_208_OUTLETS | AE | COBie | Red power equipment branch 208v outlets
54 | Environment + | Maximum_Temperature | Number | Qty | Attribute | "MAXIMO ID" | MAX_TEMP | AE | COBie | Maximum temperature allowable … if applicable
55 |  | Minimum_Temperature | Number | Qty | Attribute | "MAXIMO ID" | MIN_TEMP | AE | COBie | Minimum temperature allowable … if applicable
56 |  | Temperature_Unit_of_Measure | Text | Text | Attribute | "MAXIMO ID" | TEMP_UM | AE | COBie | C or F
57 |  | Maximum_Humidity | Number | %RH | Attribute | "MAXIMO ID" | MAX_HUMIDITY | AE | COBie | Maximum humidity allowable … if applicable
58 |  | Minimum_Humidity | Number | %RH | Attribute | "MAXIMO ID" | MIN_HUMIDITY | AE | COBie | Minimum humidity allowable … if applicable
59 |  | Air_Changes_Per_Hour | Number | Qty | Attribute | "MAXIMO ID" | AIR_CHANGES_PER_HOUR | AE | COBie | Number of air changes per hour
60 |  | Air_Pressure_Difference | Number | Qty | Attribute | "MAXIMO ID" | AIR_PRESSURE_DIFF | AE | COBie | Difference in pressure from atmospheric (+ or -)
61 |  | Air_Pressure_Unit_of_Measure | Text | Text | Attribute | "MAXIMO ID" | AIR_PRESSURE_UM | AE | COBie | PSI, Pa, mb, Hg, Atm
62 | Med Gas + | Number_of_Manifolds | Number | Ea | Attribute | "MAXIMO ID" | NUMBER_MANIFOLDS | AE | COBie | Number of manifolds … presence specified separately
63 |  | Nitrogen | Number | Y/N | Attribute | "MAXIMO ID" | NITROGEN | AE | COBie | Presence of outlet
64 |  | Medical_Air | Number | Y/N | Attribute | "MAXIMO ID" | MEDICAL_AIR | AE | COBie | Presence of outlet
65 |  | Oxygen | Number | Y/N | Attribute | "MAXIMO ID" | OXYGEN | AE | COBie | Presence of outlet
66 |  | Nitrous_Oxide | Number | Y/N | Attribute | "MAXIMO ID" | NITROUS_OXIDE | AE | COBie | Presence of outlet
67 |  | Carbon_Dioxide | Number | Y/N | Attribute | "MAXIMO ID" | CARBON_DIOXIDE | AE | COBie | Presence of outlet
68 |  | Helium | Number | Y/N | Attribute | "MAXIMO ID" | HELIUM | AE | COBie | Presence of outlet
69 |  | HEPA_Filter_Type | Text | N/A | Attribute | "MAXIMO ID" | HEPA_FILTER_TYPE | AE | COBie | Type if present
70 |  | Vacuum | Number | Y/N | Attribute | "MAXIMO ID" | VACUUM | AE | COBie | Presence of outlet
71 |  | (WAG) Waste Anesthesia Gas Disposal | Number | Y/N | Attribute | "MAXIMO ID" | WASTE_ANESTHESIA_GAS_DISPOSAL | AE | COBie | Presence of outlet

## 3.1 Asset Attribute Scope
|  |  |  | VA BIM STANDARD OmniClass Table 23 Asset Attribute Scope - v1.0 | [73 empty] | 23
|  | OmniClass | Description | Attribute Groups | [73 empty] | Definition
[23 empty] | Operating + | [10 empty] | Composition + |  |  |  |  | Dimension + | [6 empty] | Entry Devices + |  |  |  |  | Tanks + | [7 empty] | Input + |  |  |  |  | Output + | [7 empty] | Rated +
Item Number | OmniClass Level |  |  | Basic object + | Criticality | Condition + | Quantity | Type | Manufacturer | Model Number | Serial Number | Warranty | Documents + | Installation + | Service life | Blast Rating | Fire Rating | Security Level | Voltage | Amperage | Wattage | Electrical Phase | Frequency | Power factor | KVA | Circuit Branch | Gas Type | Pressure | Temperature | RPM | HP | Fuel | Water Test + | Material | Finish | Color | Length | Width | Height | Depth | Size | Thickness | Hardware Set | Operation | Glazed | Louvered | Protection Factor | Interior/Exterior | Configuration | Containment Type | Stored Material | Penetrations | Refrigerant + | Luminaries + | Key Code + | Control | Input Amps | Input Volts | Inlet Size | Inlet Pressure | Inlet Flow (Air) | Outlet Size | Outlet Pressure | Outlet Flow (Air) | Output Amps | Output Volts | Rated Temperature | Rated Pressure | Rated Flow (Liquid) | Rated Coverage | Input Rating | Output Rating | Rated Amps | Rated Volts | Load Rating | Capacity | Capacity Unit of Measure
1 | 3 | 23-11 25 11 | Perimeter Entry Devices | • | • | • | • | • | • | • |  | • | • | • | • | • | [17 empty] | • |  |  | • | • | • | • |  |  |  | • |  |  | •
2 | 3 | 23-13 39 11 | Exterior Roof Panels | • | • | • | • | • | • | • |  | • | • | • | • | • | • | [16 empty] | • | • | • | • | • | • | • |  |  |  | •
3 | 3 | 23-13 39 17 | Roof Tiles | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • | • | • | [5 empty] | •
4 | 3 | 23-13 39 23 | Flat Roofing | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • | • | • | [5 empty] | •
5 | 3 | 23-13 39 31 | Roof Membranes | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • | • | • | [5 empty] | •
6 | 2 | 23-17 11 00 | Doors | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • | • | • | • | • | • | • |  | • | • | • |  | • |  | • | [6 empty] | • | [22 empty] | A hinged, pivoted or sliding member, permitting passage through a wall.
7 | 2 | 23-17 13 00 | Windows | • | • | • | • | • | • | • |  | • | • | • | • | • | • | [16 empty] | • |  |  | • | • | • | • |  |  |  | • |  |  |  | • | [29 empty] | An opening in a wall for light and ventilation, with all its paraphernalia
8 | 2 | 23-17 17 00 | Skylights | • | • | • | • | • | • | • |  | • | • | • | • | • | • | [16 empty] | • |  | • | • | • | • | • | • |  |  | • | [33 empty] | An opening in a roof or ceiling for admitting daylight. Includes: Roof lights
9 | 3 | 23-17 21 15 | Fire and Smoke Shutters and Curtains | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • |  |  | • | • | • | • | • | • |  | • | [7 empty] | •
10 | 3 | 23-21 21 13 | Commercial Food Cooking Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [9 empty] | • |  |  |  |  | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | •
11 | 3 | 23-21 21 19 | Commercial Dishwasher Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [10 empty] | • |  |  |  | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | • | •
12 | 3 | 23-21 21 27 | Commercial Refrigerators And Freezers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • |  |  | • | [7 empty] | • | • | • | • |  |  |  | • | [8 empty] | • |  |  |  | • | • | • | • | •
13 | 3 | 23-21 21 29 | Commercial Ice Machines | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • |  |  | • |  |  |  | • |  |  |  | • | • | • | • |  |  |  | • | [8 empty] | • |  |  |  | • | • | • | • | • | •
14 | 4 | 23-21 35 21 11 | Safes | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | [15 empty] | • |  |  | • | • | • | • |  |  |  | • | [10 empty] | •
15 | 4 | 23-21 35 21 15 | Vault Doors | • | • | • | • | • | • | • | • | • | • | • | • | • | • | • | [15 empty] | • |  |  | • | • | • | • |  | • |  | • |  |  | • | [7 empty] | •
16 | 3 | 23-21 41 31 | Commercial Laundry Dryers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [6 empty] | • |  |  |  |  | • |  |  | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | •
17 | 3 | 23-21 41 41 | Commercial Washing Machines | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [14 empty] | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | • | • | •
18 | 2 | 23-21 45 00 | Historic Preservation Products | • | • | • | • | • |  |  |  |  | • | • | [19 empty] | • | [43 empty] | Historical documents and high value original art work.
19 | 3 | 23-23 11 11 | Elevators | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  |  |  |  | • |  |  |  | • | [10 empty] | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | • | [16 empty] | Elevators are selected by type of traction or hydraulic and then function.
20 | 3 | 23-23 11 13 | Escalators | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • | [10 empty] | • | • | • | • | • | [15 empty] | • | • | • | • | •
21 | 4 | 23-23 13 11 17 | Patient Lifts | • | • | • | • | • | • | • | • | • | • | • | • | [25 empty] | • |  |  | • | [12 empty] | • | • | • | • | • | [11 empty] | • |  | •
22 | 4 | 23-23 13 11 25 | Wheel Chair Lifts | • | • | • | • | • | • | • | • | • | • | • | • | [25 empty] | • |  |  | • | [12 empty] | • | • | • | • | • | [13 empty] | •
23 | 3 | 23-23 17 11 | Dumbwaiters | • | • | • | • | • | • | • | • | • | • | • | • | [21 empty] | • | • | • | • | • | [15 empty] | • | • | • | • | • | [13 empty] | •
24 | 3 | 23-23 17 17 | Chutes | • | • | • | • | • |  |  |  |  | • | • | • |  | • | [19 empty] | • | • | • | • | • |  |  | • | [14 empty] | • |  |  | •
25 | 3 | 23-23 17 21 | Pneumatic Tube Systems | • | • | • | • | • | • | • | • | • | • | • | • | [18 empty] | • |  |  | • | • | • | • | • |  |  | • | [14 empty] | • | • |  | • | • |  |  |  |  | •
26 | 3 | 23-23 17 23 | Cranes | • | • | • | • | • | • | • | • | • | • | • | • | [21 empty] | • | • | • | • | • |  |  | • |  |  |  |  | • | [25 empty] | •
27 | 3 | 23-23 17 27 | Hoists | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [14 empty] | • | • | • | • | • | [7 empty] | • | [7 empty] | • | • | • | • | • | [13 empty] | •
28 | 3 | 23-23 23 13 | Dock Levelers | • | • | • | • | • | • | • | • | • | • | • | • | [25 empty] | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | •
29 | 3 | 23-23 23 15 | Loading Dock Lifts | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [18 empty] | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | [13 empty] | •
30 | 3 | 23-23 23 23 | Loading Dock Vehicle Restraints | • | • | • | • | • | • | • | • | • | • | • | • | [18 empty] | • | [6 empty] | • |  |  | • | [30 empty] | •
31 | 3 | 23-25 13 13 | Audiology Prefabricated Structures | • | • | • | • | • | • | • | • | • | • | • | • |  | • | [19 empty] | • | • | • | • |  |  |  | • | [12 empty] | • | • | • | • | •
32 | 4 | 23-25 15 11 11 | Postmortem Refrigerators and Freezers | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  |  |  |  | • |  |  |  | • | [10 empty] | • | • | • | • | • |  |  | • | [8 empty] | • |  |  |  | • | • | • | • | •
33 | 5 | 23-25 21 13 17 19 | Emergency Medical First Response Kits | • | • | • | • | • | • | • |  |  | • | • | • | [25 empty] | • |  |  | •
34 | 3 | 23-25 23 13 | Endocrinology Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • | [6 empty] | • |  |  |  | • | • | • | • | • |  |  | • | [12 empty] | • | • | • | • | •
35 | 4 | 23-25 31 11 11 | Blood Refrigerators and Freezers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • | [10 empty] | • | • | • | • | • |  |  | • | [8 empty] | • |  |  |  | • | • | • | • | •
36 | 3 | 23-25 33 11 | Medical Air Pressure Control Cabinets | • | • | • | • | • | • | • |  |  | • | • | • | [21 empty] | • | • | • | • | • |  |  | •
37 | 3 | 23-25 33 13 | Medical Gas Alarm Modules | • | • | • | • | • | • | • | • | • | • | • | • | [11 empty] | • | [13 empty] | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | •
38 | 3 | 23-25 33 33 | Medical Gas Valve Boxes | • | • | • | • | • | • | • |  | • | • | • | • | [11 empty] | • | [13 empty] | • |  |  | • |  |  |  |  | • | [9 empty] | • | •
39 | 4 | 23-25 35 13 11 | Nursing Station Telecommunications Equipment | • | • | • | • | • | • | • |  | • | • | • | • | [28 empty] | • |  |  |  |  | • | [7 empty] | • | • | • | • | •
40 | 3 | 23-25 57 11 | Sterilizer Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [17 empty] | • |  |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • |  |  |  | •
41 | 4 | 23-25 63 11 13 | X Ray and Imagery Protective Barriers | • | • | • | • | • | • | • |  |  | • | • | [22 empty] | • | • | • | • |  | • |  | • |  |  | • |  | •
42 | 3 | 23-25 63 13 | X Ray and Imagery Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • | [10 empty] | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | •
43 | 2 | 23-25 65 00 | Biological Protection and Preservation Products | • | • | • | • | • | • | • |  |  | • | • | • | [21 empty] | • | • | • | • |  |  |  | • |  |  |  |  | • | [28 empty] | Furnishings specific to medical and laboratory.
44 | 3 | 23-25 67 11 | Hazardous Materials Cabinets | • | • | • | • | • | • | • |  | • | • | • | • |  | • | [16 empty] | • |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [5 empty] | •
45 | 3 | 23-25 67 13 | Hazardous Materials Refrigerators and Freezers | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  |  |  |  | • |  |  |  | • | [10 empty] | • | • | • | • |  |  |  | • | [8 empty] | • |  |  |  | • | • | • | • | •
46 |  | 23-25 69 11 15 | Laboratory Fume hoods | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  |  |  |  | • |  |  |  | • | [7 empty] | • |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • | •
47 | 2 | 23-27 11 00 | General Instruments and Controls | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  | • | • | [20 empty] | • |  |  | • |  |  |  |  | • | [6 empty] | • | • | • | • | • | • | [16 empty] | Instruments and controls used in multiple disciplines.
48 | 2 | 23-27 13 00 | Control and Monitoring Boards Panels | • | • | • | • | • | • | • | • | • | • | • | • |  | • |  | • | • |  | • |  |  |  | • | [14 empty] | • |  |  | • |  |  |  |  | • | [6 empty] | • | • | • | • | • | • | [9 empty] | • | [6 empty] | Control and monitoring boards panels used in multiple disciplines.
49 | 2 | 23-27 15 00 | Building Automation and Control | • | • | • | • | • | • | • |  |  | • | • | • | [25 empty] | • |  |  | • |  |  |  |  | • | [6 empty] | • | • | • | • | • | • | [16 empty] | Building automation and control equipment used in multiple disciplines.
50 | 2 | 23-27 17 00 | Pumps | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • |  |  |  | • | • | [9 empty] | • |  |  | • | [12 empty] | • | • | • | • | • | • | • |  |  |  | • | • | • | [8 empty] | Devices used to move fluids, such as liquids or gases.
51 | 2 | 23-27 19 00 | Engines | • | • | • | • | • | • | • | • | • | • | • | • | [14 empty] | • | • | • |  |  |  |  | • | • | • | • | • |  |  | • |  |  |  |  | • | [28 empty] | Machines designed to convert energy into useful mechanical motion
52 | 2 | 23-27 21 00 | Compressors | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • |  |  |  |  | • | • |  |  |  |  | • | • | • | • | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • | • |  |  | • | • | [9 empty] | Mechanical products that increase the pressure of a gas by reducing its volume.
53 | 2 | 23-27 23 00 | Heat Exchangers | • | • | • | • | • | • | • | • | • | • | • | • | [5 empty] | • | [12 empty] | • |  |  | • | • | • | • | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • | • | [13 empty] | Products built for efficient heat transfer from one medium to another.
54 | 2 | 23-27 25 00 | Heaters for Supplied Liquids | • | • | • | • | • | • | • | • | • | • | • | • | [5 empty] | • | [15 empty] | • | • | • | • | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • | [5 empty] | • | [8 empty] | Products used to heat supplied liquids.
55 | 2 | 23-27 27 00 | Pressure Reducing Stations | • | • | • | • | • | • | • |  | • | • | [27 empty] | • |  |  | • |  |  |  |  | • | [9 empty] | • | • |  | • | • | [14 empty] | Products used to reduce pressure at a station.
56 | 2 | 23-27 29 00 | Tanks and Storage Structures | • | • | • | • | • | • | • |  | • | • | • | • | [17 empty] | • | • |  |  | • | • | • | • | • | • |  | • |  |  |  |  | • | • | • | [7 empty] | • | • | • | • | • | • |  |  |  | • | [9 empty] | Prefabricated structures used to hold fluids or gases.
57 | 2 | 23-27 31 00 | Valves | • | • | • | • | • | • | • |  | • | • | • | • | [17 empty] | • | • | [6 empty] | • |  |  | • |  |  |  |  | • | [9 empty] | • | • |  | • | • | [14 empty] | Products regulating the flow fluids by opening, closing, or partially obstructing various passageways. See: Plumbing Specific Products and Equipment.
58 | 2 | 23-27 33 00 | Valve Actuators | • | • | • | • | • | • | • |  | • | • |  | • | [26 empty] | • |  | • |  |  |  |  | • | [6 empty] | • | • | • | [19 empty] | Products utilizing a source of power to operate a valve. All Valve Actuators are DDC or non-DDC.
59 | 2 | 23-27 35 00 | Variable Speed Drives | • | • |  | • | • | • | • | • | • | • | • | • | [14 empty] | • | [10 empty] | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | [19 empty] | Products used for controlling the rotational speed of an alternating current (AC) electric motor by controlling the electrical power supplied to the motor.
60 | 2 | 23-27 37 00 | Liquid Traps | • | • | • | • | • | • | • |  |  | • | • | • | [25 empty] | • |  |  | • |  |  |  |  | • | • | [8 empty] | • |  |  | • | [6 empty] | • | [8 empty] | Products which trap liquids.
61 | 4 | 23-27 55 11 11 | Water Filters | • | • | • | • | • | • | • |  |  | • | • | • | [25 empty] | • | [17 empty] | • |  |  | • | [6 empty] | •
62 | 4 | 23-27 55 29 19 | Reverse Osmosis Units | • | • | • | • | • | • | • |  |  | • | • | • | [17 empty] | • | [7 empty] | • | [15 empty] | • | • | • | • |  | • | • |  |  |  | • | • | •
63 | 4 | 23-27 55 31 11 | Liquid Chemical Feeders | • | • | • | • | • | • |  |  | • | • | • | • | [18 empty] | • | [6 empty] | • |  |  | • | [12 empty] | • | • | • |  |  | • | [5 empty] | • | • |  | •
64 | 4 | 23-27 55 31 13 | Solid Chemical Feeders | • | • | • | • | • | • | • |  | • | • | • | • | [25 empty] | • |  |  | • | [12 empty] | • | • | • |  |  | •
65 | 4 | 23-27 55 31 15 | Gas Chemical Feeders | • | • | • | • | • | • | • |  | • | • | • | • | [11 empty] | • | [13 empty] | • |  |  | • | [12 empty] | • | • | • | • |  | • | •
66 | 3 | 23-27 57 19 | Air Scrubbers | • | • | • | • | • | • | • |  | • | • | • | • | [17 empty] | • | • | [6 empty] | • |  |  | • | [11 empty] | •
67 | 3 | 23-27 57 27 | Air Filters | • | • | • | • | • | • | • |  |  | • | • | • | [18 empty] | • |  |  | • | • | • | • | • | [18 empty] | • | • |  | • | •
68 | 3 | 23-27 57 29 | Dust Collectors | • | • | • | • | • | • | • |  |  | • | • | • | [18 empty] | • | [6 empty] | •
69 | 2 | 23-27 59 00 | Recycling Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [21 empty] | • | • | • | • |  |  |  | • | [33 empty] | Equipment used in the recycling process.
70 | 2 | 23-27 61 00 | Incinerators | • | • | • | • | • | • | • | • | • | • | • | • | [13 empty] | • |  |  | • |  |  |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [28 empty] | A waste treatment product that involves the combustion of organic materials and/or substances. A furnace for incinerating (especially to dispose of refuse of a substance).
71 | 2 | 23-27 63 00 | Mechanical Insulation and Linings | • | • | • | • | • |  |  |  |  | • | • | • | [18 empty] | • | [43 empty] | Equipment used for mechanical insulation and lining.
72 | 2 | 23-27 67 00 | Corrosion Proofing Equipment | • | • | • | • | • | • |  |  | • | • |  | • | [18 empty] | • | [6 empty] | • | [36 empty] | Equipment used to prevent corrosion.
73 | 3 | 23-27 71 21 | Fall Arrest Systems | • | • | • | • | • | • | • | • | • | • | • | • | [18 empty] | • | [40 empty] | •
74 | 3 | 23-29 11 11 | Closed Circuit Television Equipment | • | • | • | • | • | • | • |  | • | • | • | • | [28 empty] | • |  |  |  |  | • | [7 empty] | • | •
75 | 3 | 23-29 11 13 | Security Video Imaging System Equipment | • | • | • | • | • | • | • |  | • | • | • | • | [28 empty] | • |  |  |  |  | • | [7 empty] | • | •
76 | 3 | 23-29 25 13 | Fire Hydrants | • | • | • | • | • | • | • |  |  | • | • | • | [17 empty] | • | [7 empty] | • |  |  | • |  |  |  |  | • | [9 empty] | • | •
77 | 3 | 23-29 25 15 | Fire Hose Equipment | • | • | • | • | • | • | • |  | • | • | • | • | [21 empty] | • | • | • | • | • | [17 empty] | • | • |  | • | •
78 | 3 | 23-29 25 19 | Fire Extinguishers | • | • | • | • | • | • | • |  |  | • | • | • | [25 empty] | • |  |  | •
79 | 2 | 23-29 27 00 | Fire Ventilation Equipment | • | • | • | • | • | • | • | • | • | • | • | • | [41 empty] | • | • | • | • |  | • | • | • | [13 empty] | Equipment used to ventilate in the event of fire.
80 | 2 | 23-29 29 00 | Fire Detection Devices | • | • | • | • | • | • | • |  |  | • | • | • |  |  |  | • | [9 empty] | • | [40 empty] | • | [7 empty] | Products used to detect a fire.
81 | 3 | 23-29 31 11 | Fire Alarm Annunciator Panels | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | [24 empty] | • |  |  |  |  | • | [7 empty] | • | •
82 | 3 | 23-29 31 13 | Fire Alarm Control Panels | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | [24 empty] | • |  |  |  |  | • | [7 empty] | • | •
83 | 3 | 23-29 31 15 | Audible Fire Notification Devices | • | • | • | • | • | • | • |  |  | • | • | • |  |  |  | • | [37 empty] | • | •
84 | 3 | 23-29 31 17 | Visible Fire Notification Devices | • | • | • | • | • | • | • |  |  | • | • | • |  |  |  | •
85 | 3 | 23-29 31 19 | Combination Audible and Visible Fire Notification Devices | • | • | • | • | • | • | • |  |  | • | • | • |  |  |  | • | [37 empty] | • | • | [11 empty] | •
86 | 3 | 23-29 31 21 | Fire Alarm Communicators | • | • | • | • | • | • | • |  |  | • | • | • |  |  |  | •
87 | 3 | 23-29 31 23 | Fire Alarm Central Stations | • | • | • | • | • | • | • |  |  | • | • | •
88 | 2 | 23-29 33 00 | Fire Suppression System Components | • | • | • | • | • | • | • |  | • | • | • | • | [62 empty] | Components specific to fire suppression when protecting the facility and occupant from harm.
89 | 3 | 23-29 37 13 | Emergency Eye Wash Stations | • | • | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | •
90 | 3 | 23-29 37 15 | Emergency Showers | • | • | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | •
91 | 2 | 23-31 11 00 | Faucets | • | • | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [5 empty] | • | [8 empty] | is a valve controlling release of liquids or gas.
92 | 2 | 23-31 13 00 | Sinks | • |  | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [14 empty] | is a bowl-shaped fixture that is used for washing the hands or small objects.
93 | 2 | 23-31 15 00 | Bathtubs | • |  | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [5 empty] | • | [8 empty] | is a plumbing fixture used for bathing
94 | 2 | 23-31 17 00 | Showers | • |  | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [14 empty] | is an area in which one bathes underneath a spray of water.
95 | 2 | 23-31 19 00 | Toilets | • |  | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [14 empty] | a plumbing fixture and disposal system primarily intended for the disposal of the bodily wastes
96 | 2 | 23-31 21 00 | Urinals | • |  | • | • | • | • | • |  | • | • | • | • | [43 empty] | • | • |  | • | • | [14 empty] | is a specialized toilet for urinating into generally used by males from a standing position.
97 | 2 | 23-31 27 00 | Floor Drains | • |  | • | • | • |  |  |  |  | • | • | • | [25 empty] | • | [27 empty] | • | [8 empty] | is a plumbing fixture installed in the floor of a structure or space, mainly designed to remove any standing water near it.
98 | 2 | 23-31 29 00 | Hot Water Heaters | • | • | • | • | • | • | • | • | • | • | • | • | [41 empty] | • | • | • | • |  | • | • | [14 empty] | A tank for heating and storing hot water.
99 | 2 | 23-31 31 00 | Drinking Fountains | • |  | • | • | • | • | • |  | • | • | • | • | [41 empty] | • | • | • | • |  | • | • | [14 empty] | A device which provides a jet of drinking water for public use.
100 | 2 | 23-33 11 00 | Commercial Boilers | • | • | • | • | • | • | • | • | • | • | • | • | [12 empty] | • | • |  |  | • |  |  |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | • | • |  | • | • |  |  |  | • | • | • |  | • | [6 empty] | a closed vessel in which water or other fluid is heated on a commercial scale
101 | 2 | 23-33 13 00 | Furnaces | • | • | • | • | • | • | • | • | • | • | • | • | [13 empty] | • |  |  | • |  |  |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [9 empty] | • |  |  | • |  |  |  |  | • | [10 empty] | is a device used for heating.
102 | 2 | 23-33 17 00 | Heat Pumps | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [21 empty] | • | [8 empty] | • |  |  |  | • | • | • |  |  | • | [15 empty] | a device that moves heat from one location (the 'source') to another location (the 'sink' or 'heat sink') using mechanical work.
103 | 2 | 23-33 19 00 | Cooling and Freeze Components | • | • | • | • | • | • | • |  | • | • | • | • | [25 empty] | • | [11 empty] | • |  |  |  | • | • | [19 empty] | Components used in the cooling and freezing cycle.
104 | 2 | 23-33 21 00 | Chillers | • | • | • | • | • | • | • |  | • | • | • | • | [21 empty] | • | • | • | • | [12 empty] | • |  |  |  | • | • | • | • |  | • | • |  |  |  | • |  | • | [8 empty] | is a product that removes heat from a liquid via a vapor-compression or absorption refrigeration cycle.
105 | 2 | 23-33 23 00 | Cooling Towers | • | • | • | • | • | • | • |  | • | • | • | • | [17 empty] | • |  |  |  | • | • | • | • |  |  |  | • |  |  |  |  | • | [9 empty] | • | • |  | • | [6 empty] | • | [8 empty] | heat removal devices used to extract waste heat to the atmosphere.
106 | 2 | 23-33 25 00 | Air Handling Units | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  |  | • | [14 empty] | • | [15 empty] | • | • |  | • | • | • | • | • | [13 empty] | is a device used to condition and circulate air as part of an HVAC system.
107 | 2 | 23-33 27 00 | Air Humidity Control Equipment | • | • | • | • | • | • | • | • | • | • | • | • |  |  |  | • | [24 empty] | • |  |  |  |  | • | [6 empty] | • | • | • | [19 empty] | Equipment used in the control of humidity.
108 | 2 | 23-33 29 00 | HVAC Dampers | • | • | • | • | • | • | • | • | • | • | • | • | [25 empty] | • |  |  | • |  |  |  |  | • | [7 empty] | • | • | • |  | • | • |  | • | [13 empty] | Devices deadens, restrains, or depresses in HVAC.
109 | 2 | 23-33 31 00 | Air Circulators | • | • | • | • | • | • | • | • | • | • | • | • | [14 empty] | • | • |  |  | • | [6 empty] | • | [17 empty] | • | • | • | • | • | • | [13 empty] | Products used for the movement of air in a circulator or circuit.
110 | 3 | 23-33 39 17 | Packaged Air Conditioners | • | • | • | • | • | • | • | • | • | • | • | • | [28 empty] | • | [8 empty] | • |  |  |  | • | •
111 | 3 | 23-33 39 21 | Split System Air Conditioning Units | • | • | • | • | • | • | • | • | • | • | • | • | [28 empty] | • | [8 empty] | • |  |  |  | • | •
112 | 4 | 23-33 41 13 13 | Variable Air Volume Induction Terminal Air Units | • | • | • | • | • | • | • | • | • | • | • | • | [28 empty] | • |  |  |  |  | • | [7 empty] | • | • | • | • | • | • | • | •
113 | 2 | 23-33 53 00 | Solar Water Heating Equipment | • |  | • | • | • | • | • |  | • | • | • | • |  |  |  | • | [9 empty] | • | [7 empty] | • | • | • | • | • | [7 empty] | • | [9 empty] | • | • |  | • | • | [14 empty] | Equipment used to heat water through solar power.
114 | 3 | 23-35 11 11 | Single Unit Electrical Generators | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | [14 empty] | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | [6 empty] | • | • | [6 empty] | •
115 | 3 | 23-35 11 13 | Motor Generator Sets | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | • | [13 empty] | • | • | • | • |  |  |  | • | [12 empty] | • | • | [6 empty] | • | • | [6 empty] | • |  |  |  |  | Electromagnetic set with a mechanical driver
116 | 4 | 23-35 11 15 23 | Wind Generator Sets | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • | • | [20 empty] | • | [20 empty] | • | • | [5 empty] | • | [5 empty] | AC Generator with a wind turbine as the driver
117 | 3 | 23-35 11 17 | Photovoltaic Generators | • | • | • | • | • | • | • | • | • | • | • | • | [28 empty] | • | [20 empty] | • | • | [5 empty] | • | • |  |  |  |  | DC Generator using solar power, all solar power creates DC that is stored or converted in a DC to AC converter
118 | 3 | 23-35 13 11 | Current Transformers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  | • | [11 empty] | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | [6 empty] | • | • | • |  |  |  | • | • | •
119 | 3 | 23-35 13 15 | Electrical Network Transformers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  | • | [11 empty] | • | • | • | • | [16 empty] | • | • | [6 empty] | • | • | • |  |  |  | • | • | •
120 | 3 | 23-35 13 17 | Power Transformers | • | • | • | • | • | • | • | • | • | • | • | • | [6 empty] | • |  |  | • | [11 empty] | • | • | • | • |  |  |  | • |  |  |  |  | • | [7 empty] | • | • | [6 empty] | • | • | • |  |  |  | • | • | •
121 | 3 | 23-35 15 11 | Alternating Current (AC) Motors | • | • | • | • | • | • | • | • | • | • | • | • | [14 empty] | • | • | [9 empty] | • |  |  | • | [12 empty] | • | •
122 | 3 | 23-35 15 13 | Direct Current (DC) Motors | • | • | • | • | • | • | • | • | • | • | • | • |  |  |  | • | [10 empty] | • | • | [9 empty] | • |  |  | • | [12 empty] | • | •
123 | 3 | 23-35 19 15 | Rechargeable Batteries | • | • | • | • | • | • | • | • | • | • | • | • |  |  |  | • | • | [20 empty] | • | [15 empty] | • | • | [12 empty] | •
124 | 2 | 23-35 21 00 | Battery Chargers | • | • | • | • | • | • | • | • | • | • | • | • | [41 empty] | • | • | [6 empty] | • | • |  |  |  |  | • | • | [5 empty] | a product used to put energy into a secondary cell or usually a rechargeable battery by forcing an electric current through it.
125 | 2 | 23-35 23 00 | Power Conditioning Equipment | • | • | • | • | • | • | • | • | • | • | • | • |  |  |  |  | • |  |  |  | • | [31 empty] | • | • | • | [12 empty] | • | [6 empty] | Equipment intended to improve the quality of the power that is delivered to electrical load equipment
126 | 2 | 23-35 25 00 | Electrical Instrumentation and Controls | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • | [23 empty] | • |  |  |  |  | • | [7 empty] | • | • | [19 empty] | Instruments which measure and control electricity.
127 | 3 | 23-35 27 11 | Electrical Receptacles | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | [45 empty] | • | • | [5 empty] | • | [5 empty] | Products used to prevent electrical shock or hazards to the occupants.
128 | 2 | 23-35 29 00 | Circuit Breakers | • | • | • | • | • | • | • | • | • | • | • | • |  |  |  | • | • | [20 empty] | • |  |  | • | [12 empty] | • | • | [12 empty] | • | [6 empty] | an automatic switch designed to protect an electrical circuit from damage caused by overload or short circuit.
129 | 2 | 23-35 31 00 | Electrical Power Distribution Devices | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • | [5 empty] | • | [7 empty] | • | [9 empty] | • |  |  |  |  | • | [7 empty] | • | • | [12 empty] | • | [6 empty] | Devices used in electrical power distribution.
130 | 3 | 23-35 37 11 | Automatic Transfer Switches | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • |  | • |  |  |  | • | [17 empty] | • |  |  |  |  | • | [7 empty] | • | • | [6 empty] | • | •
131 | 3 | 23-35 37 13 | Manual Transfer Switches | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • |  | • |  |  |  | • | [17 empty] | • |  |  |  |  | • | [7 empty] | • | • | [6 empty] | • | • | [11 empty] | Transfer circuit from one power source to another
132 | 2 | 23-35 39 00 | Electric Power Protection Devices | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • | [13 empty] | • | [9 empty] | • |  |  |  |  | • | [28 empty] | Devices used in electric power protection.
133 | 2 | 23-35 43 00 | Electrical Relays | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • | • | [23 empty] | • |  |  |  |  | • | [28 empty] | Relays are electrical devices that provide operation or protection and resulting control or alarm signal.
134 | 2 | 23-35 47 00 | Electrical Lighting | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | • |  | • | [14 empty] | • | • | • | • | • |  |  |  | • | [9 empty] | • |  |  | • | • | [19 empty] | The application of light to achieve some aesthetic or practical effect.
135 | 3 | 23-37 11 11 | Communication Service Penetrations | • |  |  | • | • |  |  |  |  | • | • |  |  | • | [16 empty] | • | [6 empty] | • | [7 empty] | •
136 | 3 | 23-37 23 11 | Wireless Phone Equipment | • | • | • | • | • | • | • |  | • | • | • | • |  |  |  | •
137 | 2 | 23-37 27 00 | Emergency Communications | • | • | • | • | • | • | • |  | • | • | • | • | [28 empty] | • |  |  |  |  | • | [28 empty] | Communication and Information Equipment or systems used in the event of an emergency to quickly notify occupants .

## 3.2 Asset Attribute Definition
|  |  | VA BIM STANDARD OmniClass Table 23 Asset Attribute Definitions - v1.0 | [6 empty] | 23
Item Number | Attribute Group | Attribute | Data Type | Unit of Measure | COBie Data Field Name |  | Maximo ID | Provided By (VA) Owner | Deliverable Type | Definition
[5 empty] | COBie Tab | COBie Column |  | (AE) Arch/Eng (GC) Constructor
1 | Basic object + | Description | Text | N/A | Component | Description | DESCRIPTION | AE | COBie | Free text description
2 |  | Model Object Identifier | Number | N/A | Zone | ExtIdentifier | ASSETNUM | AE | COBie | Identifier used within system (Maximo)
3 |  | Model Object Name | Text | N/A | Component | AssetIdentifier | ASSETIDENTIFIER | GC | COBie | Free text asset identifier … more ID than description
4 |  | Object OmniClass Category | Text | N/A | Type | Category | VA_OMNI_23 | AE | COBie | Asset (Product) category based on OmniClass Table 23
5 |  | GUID | Text | N/A | Attribuite | AssetIdentifier |  | AE/GC | COBie | External ID
6 |  | Model Object Parent | Number | N/A | System | ExtIdentifier | PARENT | VA | COBie | AssetNum for Asset
7 |  | Location | Text | N/A | Space | Name | LOCATION | AE | COBie | Space ID
8 |  | Bar Code ID | Number | N/A | Component | BarCode | VA_AEMS_MERS_REFID | GC | COBie | Identification bar code. NOT data bar code.
9 | Criticality | Criticality | Number | N/A | Attribute | "MAXIMO ID" | VA_CRITICALITY | VA | COBie | VA designated Criticality code from Maximo domain list.
10 | Condition + | Condition Code | Text | N/A | Attribute | "MAXIMO ID" | CONDITION_CODE | VA | COBie | VA designated Condition code from Maximo domain list.
11 |  | Condition Assessment Date | YYYY-MM-DD | Date | Attribute | "MAXIMO ID" | CONDITION_ASSESSMENT_DATE | VA | COBie | Condition Assessment Date
12 | Quantity | Quantity | Number | Ea | Attribute | "MAXIMO ID" | QUANTITY | AE/GC | COBie | Number of asset items
13 | Type | Type | Text | N/A | Component | TypeName | TYPE | VA/AE | COBie | Fixed or moveable
14 | Manufacturer | Manufacturer | Text | N/A | Type | Manufacturer | MANUFACTURER | GC | COBie | Manufacturer
15 | Model Number | Model Number | Text | N/A | Model | ModelNumber | PLUSHMODELNUM | GC | COBie | Model number
16 | Serial Number | Serial Number | Text | N/A | Component | SerialNumber | SERIALNUM | GC | COBie | Serial number
17 | Warranty | Warranty Start | YYYY-MM-DD | Date | Component | WarrantyStartDate | WARRANTYEXPDATE | GC | COBie | Collection of multiple warranties, as necessary. Default to duration of traditional calendar dates, but adding duration unit would provide the option for using operational time, cycles, copies, etc. Future implementation will need to address more comprehensive warranty information, including durations of warranties for parts and labor by multiple vendors.
18 |  | Warranty Description | Text | N/A | Type | WarrantyDescription | WARRANTYDESC | GC | COBie
19 |  | Warranty Duration parts | Number | Months | Type | WarrantyDurationParts | PARTSWARRANTDURATION | GC | COBie
20 |  | Warranty Duration Labor | Number | Months | Type | WarrantyDurationLabor | LABORWARRANTYDURATION | GC | COBie
21 |  | Warranty Guarantor Parts | Number | Months | Type | WarrantyGuarantorParts | PARTSWARRANTYGUARANTOR | GC | COBie
22 |  | Warranty Guarantor | Number | Months | Type | WarrantyGuarantorLabor | LABORWARRANTYGUARANTOR | GC | COBie
23 | Installation + | Installed Date | YYYY-MM-DD | Date | Component | InstallationDate | INSTALLDATE | GC | COBie | Date Placed in Service (not necessarily warranty start date)
24 |  | Installed Cost | Number | $US | Attribute | "MAXIMO ID" | VA_CAPITALVALUE | GC | COBie | Actual or estimated Installed cost
25 | Service life | Service Life | Number | Years | Type | ExpectedLife | VA_LIFE_EXPECTANCY | VA/AE/GC | COBie | Expected life
26 | Blast Rating | Blast Rating | Number | PSI | Attribute | "MAXIMO ID" | BLAST_RATING | AE | COBie | Blast rating
27 | Fire Rating | Fire Rating | Number | Hours | Attribute | "MAXIMO ID" | FIRE_RATING | AE | COBie | Fire rating in hours
28 | Security Level | Security Level | Number | N/A | Attribute | "MAXIMO ID" | SECURITY_LEVEL | VA | COBie | VA designated Security Level code from Maximo domain list.
29 | Operating + | Voltage | Number | Volts | Attribute | "MAXIMO ID" | VOLTAGE | AE | COBie | Nominal operating voltage
30 |  | Amperage | Number | Amps | Attribute | "MAXIMO ID" | AMPERAGE | AE | COBie | Nominal operating amperage
31 |  | Wattage | Number | Watts | Attribute | "MAXIMO ID" | WATTAGE | AE | COBie | Nominal operating wattage
32 |  | Electrical Phases | Number | Phases | Attribute | "MAXIMO ID" | ELECTRICAL_PHASE | AE | COBie | Electrical phases
33 |  | Frequency | Number | HZ | Attribute | "MAXIMO ID" | FREQUENCY | AE | COBie | Operating frequency in HZ
34 |  | Power Factor | Number | PF | Attribute | "MAXIMO ID" | POWER_FACTOR | AE | COBie | Power factor
35 |  | KVA | Number |  | Attribute | "MAXIMO ID" | KVA | AE | COBie
36 |  | Circuit Branch | Text | N/A | Attribute | "MAXIMO ID" | CIRCUIT_BRANCH | AE | COBie | Circuit branch identifier
37 |  | Gas Type | Text | N/A | Attribute | "MAXIMO ID" | GAS_TYPE | AE | COBie | Operating gas
38 |  | Pressure | Number | PSI | Attribute | "MAXIMO ID" | PRESSURE | AE/GC | COBie | Operational pressure in PSI
39 |  | Temperature | Number | Deg F | Attribute | "MAXIMO ID" | TEMP | GC | COBie | Operational temperature in Deg F
40 |  | RPM | Number | RPM | Attribute | "MAXIMO ID" | RPM | AE/GC | COBie | Operational RPM
41 |  | HP | Number | HP | Attribute | "MAXIMO ID" | HP | AE | COBie | Operational HP
42 |  | Fuel | Text | N/A | Attribute | "MAXIMO ID" | FUEL | AE | COBie | Input fuel
43 | Water Test + | Water Test | Text | N/A | Attribute | "MAXIMO ID" | WATER_TEST | VA/AE/GC | Report | Water test identification
44 |  | Water Test Results | Number | PPM | Attribute | "MAXIMO ID" | WATER_TEST_RESULTS | VA/AE/GC | Report | Water test measurement results in PPM
45 |  | Water Test Date | YYYY-MM-DD | Date | Attribute | "MAXIMO ID" | WATER_TEST_DATE | VA/AE/GC | Report | Water test date
46 | Composition + | Material | Text | N/A | Attribute | Material | MATERIAL | AE | COBie | Predominant object composition material, not material contained or acted on (e.g. gas, liquid, or solid)
47 |  | Finish | Text | N/A | Type | Finish | FINISH | AE | COBie | Predominant finish
48 |  | Color | Text | N/A | Type | Color | COLOR | AE | COBie | Predominant color
49 | Dimension + | Length | Number | Feet | Type | NominalLength | LENGTH | AE | COBie | Nominal length
50 |  | Width | Number | Feet | Type | NominalWidth | WIDTH | AE | COBie | Nominal width
51 |  | Height | Number | Feet | Type | NominalHeight | HEIGHT | AE | COBie | Nominal height
52 |  | Depth | Number | Feet | Type | Depth | DEPTH | AE | COBie | Nominal depth
53 |  | Size | Text | N/A | Type | Size | SIZE | AE | COBie | Nominal size
54 |  | Thickness | Number | Inches | Attribute | Thickness | THICKNESS | AE | COBie | Nominal thickness
55 | Entry Devices + | Hardware Set | Text | N/A | Attribute | HardwareSetType | HARDWARE_SET | AE | COBie | Door or gate hardware set ID
56 |  | Operation | Text | N/A | Attribute | "MAXIMO ID" | OPERATION | VA | COBie | Text … in context from Maximo domain list
57 |  | Glazed | Text | Y/N | Attribute | "MAXIMO ID" | GLAZED | AE | COBie | Presence of glazing
58 |  | Louvered | Text | Y/N | Attribute | "MAXIMO ID" | LOUVERED | AE | COBie | Presence of louvers
59 |  | Protection Factor | Number | PF | Attribute | "MAXIMO ID" | PROTECTION_FACTOR | VA | COBie | Radiation Protection Factor
60 |  | Interior/Exterior | Text | N/A | Attribute | "MAXIMO ID" | INTERIOR/EXTERIOR | AE | COBie | Interior or Exterior
61 |  | Configuration | Text | N/A | Attribute | ConfigurationType | CONFIGURATION | AE | COBie | Configuration in free text
62 | Tanks + | Containment Type | Text | N/A | Attribute | "MAXIMO ID" | CONTAINMENT_TYPE | AE | COBie | Containment type from Maximo domain list
63 |  | Stored Material | Text | N/A | Attribute | "MAXIMO ID" | STORED_MATERIAL | AE | COBie | Tank contents identifier
64 |  | Penetrations | Number | Ea | Attribute | "MAXIMO ID" | PENETRATIONS | AE/GC | COBie | Number of penetrations in tank
65 | Refrigerant + | Refrigerant | Text | N/A | Attribute | "MAXIMO ID" | REFRIGERANT | AE | COBie | Refrigerant identifier from Maximo domain list
66 |  | Refrigerant Quantity | Number | Pounds | Attribute | "MAXIMO ID" | REFRIGERANT_QTY | GC | COBie | Refrigerant quantity in pounds
67 | Luminaries + | Luminaires Type | Text | N/A | Attribute | "MAXIMO ID" | LUMINAIRES_TYPE | AE | COBie | Bulb type (incandescent, fluorescent, LED, etc.)
68 |  | Luminaires Quantity | Number | Ea | Attribute | "MAXIMO ID" | LUMINAIRES_QTY | AE | COBie | Bulb count
69 | Key Code + | Key Code | Text | N/A | Attribute | "MAXIMO ID" | KEY_CODE | VA/GC | COBie | Lock key code
70 |  | Key Master | Text | N/A | Attribute | "MAXIMO ID" | KEY_MASTER | VA/GC | COBie | Master key code
71 | Control | Switches/PLCs - Quantity | Number | Ea | Attribute | "MAXIMO ID" | SWITCHES_QTY | AE/GC | COBie | Number of switches and/or PLCs (Programmable logic controllers)
72 | Input + | Input Amps | Number | Amps | Attribute | "MAXIMO ID" | INPUT_AMPS | AE | COBie | Input amperage
73 |  | Input Volts | Number | Volts | Attribute | "MAXIMO ID" | INPUT_VOLTS | AE | COBie | Input voltage
74 |  | Inlet Size | Number | Inches | Attribute | "MAXIMO ID" | INLET_SIZE | AE | COBie | Inlet size in inches
75 |  | Inlet Pressure | Number | PSI | Attribute | "MAXIMO ID" | INLET_PRESSURE | AE/GC | COBie | Inlet pressure in PSI
76 |  | Inlet Flow (Air) | Number | CFM | Attribute | "MAXIMO ID" | INLET_FLOW_AIR | AE/GC | COBie | Inlet air flow in CFM
77 | Output + | Outlet Size | Number | Inches | Attribute | "MAXIMO ID" | OUTLET_SIZE | AE | COBie | Out size in inches
78 |  | Outlet Pressure | Number | PSI | Attribute | "MAXIMO ID" | OUTLET_PRESSURE | AE/GC | COBie | Outlet pressure in PSI
79 |  | Outlet Flow (Air) | Number | CFM | Attribute | "MAXIMO ID" | OUTLET_FLOW_AIR | AE/GC | COBie | Outlet air flow in CFM
80 |  | Output Amps | Number | Amps | Attribute | "MAXIMO ID" | OUTPUT_AMPS | AE/GC | COBie | Output amperage
81 |  | Output Volts | Number | Volts | Attribute | "MAXIMO ID" | OUTPUT_VOLTS | AE/GC | COBie | Output voltage
82 | Rated + | Rated Temperature | Number | Deg F | Attribute | "MAXIMO ID" | RATED_TEMPERATURE | AE | COBie | Rated temperature in Deg F
83 |  | Rated Pressure | Number | PSI | Attribute | "MAXIMO ID" | RATED_PRESSURE | AE/GC | COBie | Rated pressure in PSI
84 |  | Rated Flow (Liquid) | Number | GPM | Attribute | "MAXIMO ID" | RATED_FLOW_LIQUID | AE/GC | COBie | Rated flow in GPM
85 |  | Rated Coverage | Number | SF | Attribute | "MAXIMO ID" | RATED_COVERAGE | AE | COBie | Rated coverage in SF
86 |  | Input Rating | Number | Volts | Attribute | "MAXIMO ID" | INPUT_RATING | AE | COBie | Rated voltage input
87 |  | Output Rating | Number | Volts | Attribute | "MAXIMO ID" | OUTPUT_RATING | AE | COBie | Rated voltage output
88 |  | Rated Amps | Number | Amps | Attribute | "MAXIMO ID" | RATED_AMPS | AE | COBie | Rated amperage
89 |  | Rated Volts | Number | Volts | Attribute | "MAXIMO ID" | RATED_VOLTS | AE | COBie | Rated voltage
90 |  | Load Rating | Number | Pounds | Attribute | "MAXIMO ID" | LOAD_RATING | AE | COBie | Load rating
91 |  | Capacity | Number | Specified | Attribute | "MAXIMO ID" | CAPACITY | AE | COBie | Rated capacity
92 |  | Capacity Unit of Measure | Text | N/A | Attribute | "MAXIMO ID" | CAPACITY_UM | AE | COBie | Companion Capacity Unit of Measure … gallons, pounds, cut, etc.
93 | Documents + | Name | Text | N/A | Document | Name |  | GC | COBie | Document name for facilities handover including photos, O&M Manuals, Warranties, Operation Manuals, etc
94 |  | Category | Text | N/A | Document | Category |  | GC | COBie | Type of documentation
95 |  | Directory | Text | N/A | Document | Directory |  | GC | COBie | Directory location of files
96 |  | File | Text | N/A | Document | File |  | GC | COBie | File name

## Sheet1 (hidden)
CHECK | RELEASE INSTRUCTIONS
1 | Verify that no filters have been set
2 | Check the Protect Worksheet Settings in "Protect Worksheet" to enable:
Select locked cells
Select unlocked cells
Use AutoFilter
Use PivotTable Reports
3 | Check filters haven't been set